## Sheet1
| 30019 | 30020 | 30021 | 30022 | 30023 | 30024 | 30025 | 30026 | 30027 | 30028 | 30029 | 30030 | 30031 | 30032 | 30033 | 30034 | 30035 | 30036 | 30037 | 30038 | 6318
| Streaming Current | Aluminum Sulfate Dose | Catfloc 8103+ Dose | Plant Influent Flow | Raw Water Turbidity | Raw Water pH | Raw Water Alkalinity | Raw Water TOC | Raw Water Temperature | Settled Water Turbidity | Combined Filter Effluent Turbidity | Filter Average Run Time | Filter Average UFRV | Finished Water pH | Finished Water Alkalinity | Finished Water TOC | Reclaim Water Flow | Reclaim Water Flow as Percentage of Plant Influent | Rapid Mix pH | Zeta Potential | Rapid Mix Sodium Permanganate Residual | Signal Health
Date | mV | mg/L | mg/L | MGD | NTU | SU | mg/L | mg/L | Deg F | NTU | NTU | Hours | gal/ft^2 | SU | mg/L | mg/L | gpm | % | SU | mV | mg/L | %
7/29/2025 16:00 | 4 | 19 | 2.75 | 8.058 | 3.306 | 7.19 | 55 | 2.03 | 68.7 | 0.27 | 0.02 | 47.57 | 11030 | 8.19 | 58 | 1.49 | 82.36 | 1.47 | 6.82 | -2.981 | 0.31
7/29/2025 16:15 | 5 | 19 | 2.75 | 8.074 | 3.267 | 7.19 | 55 | 2.03 | 68.7 | 0.27 | 0.02 | 47.57 | 11030 | 8.19 | 58 | 1.49 | 84.34 | 1.5 | 6.81 | -2.981 | 0.31
7/29/2025 16:30 | 8 | 19 | 2.75 | 8.033 | 4.3 | 7.19 | 55 | 2.03 | 68.7 | 0.27 | 0.02 | 47.57 | 11030 | 8.18 | 58 | 1.49 | 84.3 | 1.51 | 6.81 | -2.981 | 0.31
7/29/2025 16:45 | 11 | 19 | 2.75 | 7.362 | 3.873 | 7.18 | 55 | 2.03 | 68.7 | 0.27 | 0.02 | 47.57 | 11030 | 8.17 | 58 | 1.49 | 76.57 | 1.5 | 6.81 | -2.981 | 0.3
7/29/2025 17:00 | 12 | 19 | 2.75 | 7.397 | 3.663 | 7.17 | 55 | 2.03 | 68.7 | 0.27 | 0.019 | 47.57 | 11030 | 8.15 | 58 | 1.49 | 76.22 | 1.48 | 6.83 | -2.981 | 0.31
7/29/2025 17:15 | 14 | 19 | 2.75 | 7.791 | 3.511 | 7.18 | 55 | 2.03 | 68.7 | 0.27 | 0.019 | 47.57 | 11030 | 8.13 | 58 | 1.49 | 81.28 | 1.5 | 6.84 | -2.981 | 0.31
7/29/2025 17:30 | 14 | 19 | 2.75 | 7.824 | 3.546 | 7.18 | 55 | 2.03 | 68.7 | 0.27 | 0.019 | 47.57 | 11030 | 8.15 | 58 | 1.49 | 81.32 | 1.5 | 6.84 | -2.981 | 0.32
7/29/2025 17:45 | 13 | 19 | 2.75 | 7.788 | 3.354 | 7.18 | 55 | 2.03 | 68.7 | 0.27 | 0.019 | 47.57 | 11030 | 8.19 | 58 | 1.49 | 81.19 | 1.5 | 6.84 | -2.981 | 0.31
7/29/2025 18:00 | 16 | 19 | 2.75 | 7.779 | 3.223 | 7.18 | 55 | 2.03 | 68.7 | 0.27 | 0.019 | 47.57 | 11030 | 8.21 | 58 | 1.49 | 81.58 | 1.51 | 6.84 | -2.981 | 0.31
7/29/2025 18:15 | 16 | 19 | 2.75 | 7.806 | 3.141 | 7.18 | 55 | 2.03 | 68.7 | 0.27 | 0.019 | 47.57 | 11030 | 8.21 | 58 | 1.49 | 81.07 | 1.5 | 6.83 | -2.981 | 0.31
7/29/2025 18:30 | 17 | 19 | 2.75 | 7.728 | 3.137 | 7.18 | 55 | 2.03 | 68.7 | 0.27 | 0.019 | 47.57 | 11030 | 8.21 | 58 | 1.49 | 80.92 | 1.51 | 6.83 | -2.981 | 0.31
7/29/2025 18:45 | 19 | 19 | 2.75 | 7.436 | 3.049 | 7.18 | 55 | 2.03 | 68.7 | 0.27 | 0.019 | 47.57 | 11030 | 8.2 | 58 | 1.49 | 77.57 | 1.5 | 6.85 | -2.981 | 0.31
7/29/2025 19:00 | 18 | 19 | 2.75 | 7.194 | 3.007 | 7.18 | 55 | 2.03 | 68.7 | 0.27 | 0.019 | 47.57 | 11030 | 8.2 | 58 | 1.49 | 75.04 | 1.5 | 6.86 | -2.981 | 0.3
7/29/2025 19:15 | 17 | 19 | 2.75 | 7.866 | 3.061 | 7.18 | 55 | 2.03 | 68.7 | 0.27 | 0.019 | 47.57 | 11030 | 8.2 | 58 | 1.49 | 82.02 | 1.5 | 6.86 | -2.981 | 0.33
7/29/2025 19:30 | 18 | 19 | 2.75 | 7.846 | 3.292 | 7.17 | 55 | 2.03 | 68.7 | 0.27 | 0.019 | 47.57 | 11030 | 8.2 | 58 | 1.49 | 82.17 | 1.51 | 6.85 | -2.981 | 0.31
7/29/2025 19:45 | 18 | 19 | 2.75 | 7.945 | 3.116 | 7.16 | 55 | 2.03 | 68.7 | 0.27 | 0.019 | 47.57 | 11030 | 8.2 | 58 | 1.49 | 82.17 | 1.49 | 6.84 | -2.981 | 0.32
7/29/2025 20:00 | 19 | 19 | 2.75 | 7.649 | 3.386 | 7.16 | 55 | 2.03 | 68.7 | 0.303 | 0.019 | 47.57 | 11030 | 8.2 | 58 | 1.49 | 80.14 | 1.51 | 6.83 | -2.981 | 0.31
7/29/2025 20:15 | 19 | 19 | 2.75 | 7.46 | 3.226 | 7.15 | 55 | 2.03 | 68.7 | 0.303 | 0.019 | 47.57 | 11030 | 8.2 | 58 | 1.49 | 154.57 | 2.98 | 6.84 | -2.981 | 0.3
7/29/2025 20:30 | 20 | 19 | 2.75 | 7.586 | 3.106 | 7.15 | 55 | 2.03 | 68.7 | 0.303 | 0.019 | 47.57 | 11030 | 8.21 | 58 | 1.49 | 157.22 | 2.98 | 6.84 | -2.981 | 0.3
7/29/2025 20:45 | 20 | 19 | 2.75 | 7.772 | 3.073 | 7.14 | 55 | 2.03 | 68.7 | 0.303 | 0.019 | 47.57 | 11030 | 8.21 | 58 | 1.49 | 162.24 | 3.01 | 6.82 | -2.981 | 0.31
7/29/2025 21:00 | 20 | 19 | 2.75 | 7.663 | 3.199 | 7.13 | 55 | 2.03 | 68.7 | 0.303 | 0.019 | 47.57 | 11030 | 8.21 | 58 | 1.49 | 157.25 | 2.95 | 6.82 | -2.981 | 0.31
7/29/2025 21:15 | 21 | 19 | 2.75 | 7.061 | 3.099 | 7.13 | 55 | 2.03 | 68.7 | 0.303 | 0.019 | 47.57 | 11030 | 8.21 | 58 | 1.49 | 147.51 | 3.01 | 6.83 | -2.981 | 0.31
7/29/2025 21:30 | 20 | 19 | 2.75 | 7.563 | 3.098 | 7.14 | 55 | 2.03 | 68.7 | 0.303 | 0.019 | 47.57 | 11030 | 8.21 | 58 | 1.49 | 157.76 | 3 | 6.84 | -2.981 | 0.31
7/29/2025 21:45 | 21 | 19 | 2.75 | 7.572 | 2.976 | 7.14 | 55 | 2.03 | 68.7 | 0.303 | 0.019 | 47.57 | 11030 | 8.22 | 58 | 1.49 | 158.1 | 3.01 | 6.83 | -2.981 | 0.31
7/29/2025 22:00 | 20 | 19 | 2.75 | 7.546 | 2.883 | 7.14 | 57 | 2.03 | 68.5 | 0.303 | 0.019 | 47.57 | 11030 | 8.22 | 58 | 1.49 | 158.14 | 3.02 | 6.82 | -2.981 | 0.31
7/29/2025 22:15 | 22 | 19 | 2.75 | 7.592 | 2.867 | 7.13 | 57 | 2.03 | 68.5 | 0.303 | 0.019 | 47.57 | 11030 | 8.22 | 58 | 1.49 | 158.31 | 3 | 6.83 | -2.981 | 0.3
7/29/2025 22:30 | 21 | 19 | 2.75 | 7.582 | 2.986 | 7.13 | 57 | 2.03 | 68.5 | 0.303 | 0.019 | 47.57 | 11030 | 8.22 | 58 | 1.49 | 157.85 | 3 | 6.82 | -2.981 | 0.31
7/29/2025 22:45 | 21 | 19 | 2.75 | 7.63 | 3.201 | 7.12 | 57 | 2.03 | 68.5 | 0.303 | 0.019 | 47.57 | 11030 | 8.22 | 58 | 1.49 | 158.18 | 2.99 | 6.81 | -2.981 | 0.33
7/29/2025 23:00 | 22 | 19 | 2.75 | 7.562 | 3.254 | 7.11 | 57 | 2.03 | 68.5 | 0.303 | 0.019 | 47.57 | 11030 | 8.22 | 58 | 1.49 | 158.03 | 3.01 | 6.81 | -2.981 | 0.32
7/29/2025 23:15 | 22 | 19 | 2.75 | 7.573 | 3.242 | 7.11 | 57 | 2.03 | 68.5 | 0.303 | 0.019 | 47.57 | 11030 | 8.23 | 58 | 1.49 | 158.37 | 3.01 | 6.81 | -2.981 | 0.32
7/29/2025 23:30 | 22 | 19 | 2.75 | 7.599 | 3.375 | 7.11 | 57 | 2.03 | 68.5 | 0.303 | 0.019 | 47.57 | 11030 | 8.23 | 58 | 1.49 | 158.32 | 3 | 6.8 | -2.981 | 0.3
7/29/2025 23:45 | 21 | 19 | 2.75 | 7.502 | 3.348 | 7.11 | 57 | 2.03 | 68.5 | 0.303 | 0.019 | 47.57 | 11030 | 8.23 | 58 | 1.49 | 154.21 | 2.96 | 6.8 | -2.981 | 0.31
7/30/2025 00:00 | 20 | 19 | 2.75 | 6.878 | 3.24 | 7.11 | 57 | 1.99 | 68.5 | 0.375 | 0.019 | 47.57 | 11030 | 8.23 | 58 |  | 144.46 | 3.02 | 6.81 | -2.981 | 0.31
7/30/2025 00:15 | 21 | 19 | 2.75 | 7.064 | 3.188 | 7.11 | 57 | 1.99 | 68.5 | 0.375 | 0.018 | 47.57 | 11030 | 8.24 | 58 |  | 146.53 | 2.99 | 6.81 | -2.981 | 0.31
7/30/2025 00:30 | 18 | 19 | 2.75 | 7.453 | 3.409 | 7.11 | 57 | 1.99 | 68.5 | 0.375 | 0.018 | 47.57 | 11030 | 8.23 | 58 |  | 154.11 | 2.98 | 6.81 | -2.981 | 0.3
7/30/2025 00:45 | 20 | 19 | 2.75 | 7.384 | 3.227 | 7.12 | 57 | 1.99 | 68.5 | 0.375 | 0.018 | 47.57 | 11030 | 8.22 | 58 |  | 154.2 | 3.01 | 6.82 | -2.981 | 0.3
7/30/2025 01:00 | 19 | 19 | 2.75 | 7.503 | 3.375 | 7.12 | 57 | 1.99 | 68.5 | 0.375 | 0.018 | 47.57 | 11030 | 8.23 | 58 |  | 155.18 | 2.98 | 6.82 | -2.981 | 0.31
7/30/2025 01:15 | 19 | 19 | 2.75 | 6.822 | 3.393 | 7.11 | 57 | 1.99 | 68.5 | 0.375 | 0.018 | 47.57 | 11030 | 8.23 | 58 |  | 142.08 | 3 | 6.82 | -2.981 | 0.3
7/30/2025 01:30 | 20 | 19 | 2.75 | 6.753 | 3.393 | 7.11 | 57 | 1.99 | 68.5 | 0.375 | 0.018 | 47.57 | 11030 | 8.23 | 58 |  | 141.01 | 3.01 | 6.81 | -2.981 | 0.3
7/30/2025 01:45 | 18 | 19 | 2.75 | 7.153 | 4.628 | 7.11 | 57 | 1.99 | 68.5 | 0.375 | 0.018 | 47.57 | 11030 | 8.22 | 58 |  | 149.32 | 3.01 | 6.81 | -2.981 | 0.3
7/30/2025 02:00 | 17 | 19 | 2.75 | 7.175 | 4.814 | 7.11 | 57 | 1.99 | 68.3 | 0.375 | 0.018 | 47.57 | 11030 | 8.22 | 59 |  | 148.39 | 2.98 | 6.81 | -2.981 | 0.3
7/30/2025 02:15 | 18 | 19 | 2.75 | 7.377 | 4.179 | 7.11 | 57 | 1.99 | 68.3 | 0.375 | 0.018 | 47.57 | 11030 | 8.22 | 59 |  | 152.99 | 2.99 | 6.82 | -2.981 | 0.3
7/30/2025 02:30 | 17 | 19 | 2.75 | 7.291 | 3.701 | 7.12 | 57 | 1.99 | 68.3 | 0.375 | 0.018 | 47.57 | 11030 | 8.22 | 59 |  | 153.03 | 3.02 | 6.82 | -2.981 | 0.3
7/30/2025 02:45 | 18 | 19 | 2.75 | 7.305 | 3.499 | 7.12 | 57 | 1.99 | 68.3 | 0.375 | 0.018 | 47.57 | 11030 | 8.22 | 59 |  | 153.52 | 3.03 | 6.84 | -2.981 | 0.3
7/30/2025 03:00 | 17 | 19 | 2.75 | 7.785 | 3.267 | 7.13 | 57 | 1.99 | 68.3 | 0.375 | 0.019 | 47.45 | 11035 | 8.23 | 59 |  | 162.16 | 3 | 6.83 | -2.981 | 0.15
7/30/2025 03:15 | 22 | 19 | 2.75 | 7.778 | 3.28 | 7.12 | 57 | 1.99 | 68.3 | 0.375 | 0.02 | 47.45 | 11035 | 8.23 | 59 |  | 162.38 | 3.01 | 6.82 | -2.981 | 0.3
7/30/2025 03:30 | 21 | 19 | 2.75 | 7.891 | 3.203 | 7.12 | 57 | 1.99 | 68.3 | 0.375 | 0.02 | 47.45 | 11035 | 8.23 | 59 |  | 162.6 | 2.97 | 6.83 | -2.981 | 0.29
7/30/2025 03:45 | 20 | 19 | 2.75 | 7.825 | 3.072 | 7.13 | 57 | 1.99 | 68.3 | 0.375 | 0.019 | 47.45 | 11035 | 8.22 | 59 |  | 162.14 | 2.98 | 6.84 | -2.981 | 0.29
7/30/2025 04:00 | 18 | 19 | 2.75 | 7.747 | 3.256 | 7.13 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.18 | 59 |  | 162.09 | 3.01 | 6.85 | -2.981 | 0.29
7/30/2025 04:15 | 20 | 19 | 2.75 | 7.776 | 3.423 | 7.13 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.16 | 59 |  | 161.86 | 3 | 6.84 | -2.981 | 0.31
7/30/2025 04:30 | 18 | 19 | 2.75 | 7.911 | 3.507 | 7.12 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.16 | 59 |  | 162.7 | 2.96 | 6.83 | -2.981 | 0.29
7/30/2025 04:45 | 17 | 19 | 2.75 | 7.261 | 3.786 | 7.11 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.19 | 59 |  | 152.26 | 3.02 | 6.84 | -2.981 | 0.3
7/30/2025 05:00 | 18 | 19 | 2.75 | 7.358 | 3.778 | 7.11 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.2 | 59 |  | 152.71 | 2.99 | 6.83 | -2.981 | 0.33
7/30/2025 05:15 | 17 | 19 | 2.75 | 7.625 | 3.614 | 7.11 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.21 | 59 |  | 159.33 | 3.01 | 6.82 | -2.981 | 0.29
7/30/2025 05:30 | 15 | 19 | 2.75 | 7.612 | 3.56 | 7.11 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.21 | 59 |  | 159.21 | 3.01 | 6.82 | -2.981 | 0.3
7/30/2025 05:45 | 17 | 19 | 2.75 | 7.609 | 3.537 | 7.11 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.2 | 59 |  | 158.98 | 3.01 | 6.83 | -2.981 | 0.22
7/30/2025 06:00 | 18 | 19 | 2.75 | 7.6 | 3.474 | 7.11 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.19 | 59 |  | 159.41 | 3.02 | 6.82 | -2.981 | 0.33
7/30/2025 06:15 | 21 | 19 | 2.75 | 7.419 | 3.419 | 7.12 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.19 | 59 |  | 152.45 | 2.96 | 6.83 | -2.981 | 0.31
7/30/2025 06:30 | 21 | 19 | 2.75 | 7.08 | 3.786 | 7.11 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.18 | 59 |  | 147.74 | 3 | 6.83 | -2.981 | 0.31
7/30/2025 06:45 | 21 | 19 | 2.75 | 7.194 | 3.729 | 7.12 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.18 | 59 |  | 151.75 | 3.04 | 6.83 | -2.981 | 0.31
7/30/2025 07:00 | 20 | 19 | 2.75 | 7.439 | 3.405 | 7.13 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.17 | 59 |  | 155.17 | 3 | 6.83 | -2.981 | 0.33
7/30/2025 07:15 | 21 | 19 | 2.75 | 7.495 | 3.25 | 7.13 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.17 | 59 |  | 155.84 | 2.99 | 6.84 | -2.981 | 0.33
7/30/2025 07:30 | 22 | 19 | 2.75 | 7.506 | 3.953 | 7.13 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.17 | 59 |  | 155.18 | 2.98 | 6.84 | -2.981 | 0.36
7/30/2025 07:45 | 22 | 19 | 2.75 | 7.398 | 3.884 | 7.13 | 57 | 1.99 | 68.3 | 0.408 | 0.019 | 47.45 | 11035 | 8.17 | 59 |  | 154.91 | 3.02 | 6.84 | -2.981 | 0.33
7/30/2025 08:00 | 22 | 19 | 2.75 | 7.054 | 3.608 | 7.13 | 57 | 1.99 | 68.3 | 0.419 | 0.019 | 47.45 | 11035 | 8.16 | 59 |  | 145.71 | 2.97 | 6.84 | -2.981 | 0.33
7/30/2025 08:15 | 20 | 19 | 2.75 | 7.01 | 3.634 | 7.12 | 57 | 1.99 | 68.3 | 0.419 | 0.019 | 47.45 | 11035 | 8.16 | 59 |  | 148.2 | 3.04 | 6.84 | -2.981 | 0.31
7/30/2025 08:30 | 20 | 19 | 2.75 | 7.38 | 3.905 | 7.12 | 57 | 1.99 | 68.3 | 0.419 | 0.019 | 47.45 | 11035 | 8.16 | 59 |  | 153.04 | 2.99 | 6.84 | -2.981 | 0.31
7/30/2025 08:45 | 18 | 19 | 2.75 | 7.27 | 3.89 | 7.12 | 57 | 1.99 | 68.3 | 0.419 | 0.019 | 47.45 | 11035 | 8.16 | 59 |  | 151.8 | 3.01 | 6.85 | -2.981 | 0.3
7/30/2025 09:00 | 19 | 19 | 2.75 | 7.355 | 3.988 | 7.12 | 57 | 1.99 | 68.3 | 0.419 | 0.019 | 47.45 | 11035 | 8.17 | 59 |  | 152.39 | 2.98 | 6.85 | -2.981 | 0.31
7/30/2025 09:15 | 19 | 19 | 2.75 | 7.311 | 4.391 | 7.11 | 57 | 1.99 | 68.3 | 0.419 | 0.018 | 47.45 | 11035 | 8.16 | 59 |  | 152.74 | 3.01 | 6.84 | -2.981 | 0.31
7/30/2025 09:30 | 18 | 19 | 2.75 | 7.306 | 4.229 | 7.1 | 57 | 1.99 | 68.3 | 0.419 | 0.018 | 47.45 | 11035 | 8.17 | 59 |  | 152.59 | 3.01 | 6.84 | -2.981 | 0.33
7/30/2025 09:45 | 17 | 19 | 2.75 | 7.379 | 4.102 | 7.11 | 57 | 1.99 | 68.3 | 0.419 | 0.018 | 47.45 | 11035 | 8.17 | 59 |  | 153.25 | 2.99 | 6.85 | -2.981 | 0.33
7/30/2025 10:00 | 16 | 19 | 2.75 | 7.467 | 4.241 | 7.11 | 55 | 1.99 | 68.1 | 0.419 | 0.018 | 47.45 | 11035 | 8.18 | 59 |  | 152.28 | 2.94 | 6.85 | -2.981 | 0.33
7/30/2025 10:15 | 16 | 19 | 2.75 | 7.419 | 3.957 | 7.11 | 55 | 1.99 | 68.1 | 0.419 | 0.018 | 47.45 | 11035 | 8.19 | 59 |  | 152.48 | 2.96 | 6.85 | -2.981 | 0.3
7/30/2025 10:30 | 18 | 19 | 2.75 | 6.803 | 3.647 | 7.11 | 55 | 1.99 | 68.1 | 0.419 | 0.018 | 47.45 | 11035 | 8.19 | 59 |  | 141.54 | 3 | 6.85 | -2.981 | 0.31
7/30/2025 10:45 | 18 | 19 | 2.75 | 6.879 | 3.407 | 7.11 | 55 | 1.99 | 68.1 | 0.419 | 0.018 | 47.45 | 11035 | 8.2 | 59 |  | 143.23 | 3 | 6.85 | -2.981 | 0.31
7/30/2025 11:00 | 18 | 19 | 2.75 | 7.016 | 3.805 | 7.1 | 55 | 1.99 | 68.1 | 0.419 | 0.018 | 47.45 | 11035 | 8.2 | 59 |  | 145.96 | 3 | 6.86 | -2.981 | 0.31
7/30/2025 11:15 | 19 | 19 | 2.75 | 7.093 | 2.28 | 7.12 | 55 | 1.99 | 68.1 | 0.419 | 0.018 | 47.45 | 11035 | 8.2 | 59 |  | 147.06 | 2.99 | 6.86 | -2.981 | 0.31
7/30/2025 11:30 | 16 | 19 | 2.75 | 7.177 | 2.199 | 7.13 | 55 | 1.99 | 68.1 | 0.419 | 0.018 | 47.45 | 11035 | 8.21 | 59 |  | 151.14 | 3.03 | 5.9 | -2.981 | 0.3
7/30/2025 11:45 | 20 | 19 | 2.75 | 7.35 | 2.179 | 7.14 | 55 | 1.99 | 68.1 | 0.419 | 0.018 | 47.45 | 11035 | 8.21 | 59 |  | 151.85 | 2.98 | 6.5 | -2.981 | 0.28
7/30/2025 12:00 | 18 | 19 | 2.75 | 6.577 | 2.109 | 7.14 | 55 | 1.99 | 68.1 | 0.245 | 0.018 | 47.45 | 11035 | 8.21 | 59 |  | 137.7 | 3.01 | 6.61 | -2.979 | 0.31
7/30/2025 12:15 | 21 | 19 | 2.75 | 6.562 | 2.158 | 7.14 | 55 | 1.99 | 68.1 | 0.245 | 0.019 | 47.45 | 11035 | 8.21 | 59 |  | 136.6 | 3 | 6.76 | -2.979 | 0.29
7/30/2025 12:30 | 22 | 19 | 2.75 | 7.086 | 2.26 | 7.14 | 55 | 1.99 | 68.1 | 0.245 | 0.019 | 47.45 | 11035 | 8.22 | 59 |  | 148.33 | 3.01 | 6.81 | -2.979 | 0.3
7/30/2025 12:45 | 21 | 19 | 2.75 | 7.124 | 2.187 | 7.14 | 55 | 1.99 | 68.1 | 0.245 | 0.018 | 47.45 | 11035 | 8.22 | 59 |  | 146.51 | 2.96 | 6.84 | -2.979 | 0.32
7/30/2025 13:00 | 21 | 19 | 2.75 | 7.1 | 2.139 | 7.14 | 55 | 1.99 | 68.1 | 0.245 | 0.018 | 47.45 | 11035 | 8.22 | 59 |  | 146.88 | 2.98 | 6.85 | -2.979 | 0.33
7/30/2025 13:15 | 21 | 19 | 2.75 | 6.956 | 2.225 | 7.14 | 55 | 1.99 | 68.1 | 0.245 | 0.019 | 47.45 | 11035 | 8.22 | 59 |  | 147.32 | 3.05 | 6.85 | -2.979 | 0.3
7/30/2025 13:30 | 23 | 19 | 2.75 | 7.119 | 2.189 | 7.14 | 55 | 1.99 | 68.1 | 0.245 | 0.019 | 47.45 | 11035 | 8.22 | 59 |  | 146.87 | 2.97 | 6.85 | -2.979 | 0.31
7/30/2025 13:45 | 21 | 19 | 2.75 | 7.114 | 2.147 | 7.14 | 55 | 1.99 | 68.1 | 0.245 | 0.019 | 47.45 | 11035 | 8.22 | 59 |  | 147.01 | 2.98 | 6.85 | -2.979 | 0.3
7/30/2025 14:00 | 23 | 19 | 2.75 | 6.509 | 2.189 | 7.14 | 55 | 1.99 | 68.3 | 0.245 | 0.019 | 47.45 | 11035 | 8.22 | 60 |  | 135.64 | 3 | 6.84 | -2.979 | 0.29
7/30/2025 14:15 | 21 | 19 | 2.75 | 6.571 | 2.345 | 7.13 | 55 | 1.99 | 68.3 | 0.245 | 0.019 | 47.45 | 11035 | 8.22 | 60 |  | 137.69 | 3.02 | 6.83 | -2.979 | 0.3
7/30/2025 14:30 | 19 | 19 | 2.75 | 7.063 | 2.315 | 7.12 | 55 | 1.99 | 68.3 | 0.245 | 0.019 | 47.45 | 11035 | 8.22 | 60 |  | 146.72 | 2.99 | 6.82 | -2.979 | 0.31
7/30/2025 14:45 | 21 | 19 | 2.75 | 7.041 | 2.611 | 7.15 | 55 | 1.99 | 68.3 | 0.245 | 0.019 | 47.45 | 11035 | 8.22 | 60 |  | 73.35 | 1.5 | 6.82 | -2.979 | 0.35
7/30/2025 15:00 | 21 | 19 | 2.75 | 7.062 | 2.832 | 7.16 | 55 | 1.99 | 68.3 | 0.245 | 0.019 | 47.45 | 11035 | 8.21 | 60 |  | 73.04 | 1.49 | 6.82 | -2.979 | 0.31
7/30/2025 15:15 | 21 | 19 | 2.75 | 7.154 | 2.896 | 7.17 | 55 | 1.99 | 68.3 | 0.245 | 0.019 | 47.45 | 11035 | 8.21 | 60 |  | 74.05 | 1.49 | 6.82 | -2.979 | 0.31
7/30/2025 15:30 | 21 | 19 | 2.75 | 7.118 | 2.953 | 7.18 | 55 | 1.99 | 68.3 | 0.245 | 0.019 | 47.06 | 10937 | 8.2 | 60 |  | 74.13 | 1.5 | 6.83 | -2.979 | 0.32
7/30/2025 15:45 | 21 | 19 | 2.75 | 7.121 | 3.043 | 7.19 | 55 | 1.99 | 68.3 | 0.245 | 0.019 | 47.06 | 10937 | 8.2 | 60 |  | 73.89 | 1.49 | 6.84 | -2.979 | 0.31
7/30/2025 16:00 | 19 | 19 | 2.75 | 7.152 | 3.097 | 7.19 | 55 | 1.99 | 68.3 | 0.268 | 0.019 | 47.06 | 10937 | 8.2 | 60 |  | 74.11 | 1.49 | 6.83 | -2.979 | 0.31
7/30/2025 16:15 | 21 | 19 | 2.75 | 7.044 | 3.084 | 7.19 | 55 | 1.99 | 68.3 | 0.268 | 0.019 | 47.06 | 10937 | 8.2 | 60 |  | 72.66 | 1.49 | 6.84 | -2.979 | 0.31
7/30/2025 16:30 | 22 | 19 | 2.75 | 6.614 | 2.835 | 7.19 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.18 | 60 |  | 69.08 | 1.5 | 6.84 | -2.979 | 0.31
7/30/2025 16:45 | 21 | 19 | 2.75 | 6.519 | 2.665 | 7.2 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.15 | 60 |  | 67.33 | 1.49 | 6.85 | -2.979 | 0.33
7/30/2025 17:00 | 24 | 19 | 2.75 | 6.738 | 2.814 | 7.2 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.14 | 60 |  | 71.16 | 1.52 | 6.84 | -2.979 | 0.31
7/30/2025 17:15 | 22 | 19 | 2.75 | 6.876 | 2.882 | 7.2 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.16 | 60 |  | 70.26 | 1.47 | 6.83 | -2.979 | 0.31
7/30/2025 17:30 | 22 | 19 | 2.75 | 6.9 | 2.94 | 7.2 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.16 | 60 |  | 0 | 0 | 6.82 | -2.979 | 0.31
7/30/2025 17:45 | 20 | 19 | 2.75 | 6.991 | 3.235 | 7.2 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.15 | 60 |  | 0 | 0 | 6.81 | -2.979 | 0.31
7/30/2025 18:00 | 23 | 19 | 2.75 | 7.142 | 3.331 | 7.2 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.11 | 60 |  | 0 | 0 | 6.81 | -2.979 | 0.32
7/30/2025 18:15 | 23 | 19 | 2.75 | 7.119 | 3.291 | 7.2 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.1 | 60 |  | 0 | 0 | 6.82 | -2.979 | 0.3
7/30/2025 18:30 | 23 | 19 | 2.75 | 6.997 | 3.302 | 7.21 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.11 | 60 |  | 0 | 0 | 6.83 | -2.979 | 0.31
7/30/2025 18:45 | 22 | 19 | 2.75 | 6.506 | 3.627 | 7.21 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.13 | 60 |  | 0 | 0 | 6.82 | -2.979 | 0.3
7/30/2025 19:00 | 23 | 19 | 2.75 | 6.537 | 3.855 | 7.21 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.14 | 60 |  | 0 | 0 | 6.81 | -2.979 | 0.31
7/30/2025 19:15 | 22 | 19 | 2.75 | 6.932 | 3.706 | 7.2 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.15 | 60 |  | 44.04 | 0.91 | 6.8 | -2.979 | 0.32
7/30/2025 19:30 | 21 | 19 | 2.75 | 7.052 | 3.869 | 7.18 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.16 | 60 |  | 72.75 | 1.49 | 6.8 | -2.979 | 0.3
7/30/2025 19:45 | 21 | 19 | 2.75 | 6.957 | 39.936 | 7.16 | 55 | 1.99 | 68.3 | 0.268 | 0.02 | 46.32 | 10884 | 8.16 | 60 |  | 72.72 | 1.51 | 6.8 | -2.979 | 0.35
7/30/2025 20:00 | 22 | 19 | 2.75 | 6.838 | 9.741 | 7.16 | 55 | 1.99 | 68.3 | 0.29 | 0.02 | 46.32 | 10884 | 8.16 | 60 |  | 71.74 | 1.51 | 6.8 | -2.979 | 0.31
7/30/2025 20:15 | 18 | 19 | 2.75 | 6.176 | 5.332 | 7.15 | 55 | 1.99 | 68.3 | 0.29 | 0.02 | 46.32 | 10884 | 8.16 | 60 |  | 64.41 | 1.5 | 6.79 | -2.979 | 0.33
7/30/2025 20:30 | 19 | 19 | 2.75 | 5.995 | 4.622 | 7.15 | 55 | 1.99 | 68.3 | 0.29 | 0.02 | 46.32 | 10884 | 8.16 | 60 |  | 61.78 | 1.48 | 6.81 | -2.979 | 0.43
7/30/2025 20:45 | 21 | 19 | 2.75 | 6.655 | 4.82 | 7.15 | 55 | 1.99 | 68.3 | 0.29 | 0.02 | 46.32 | 10884 | 8.16 | 60 |  | 68.71 | 1.49 | 6.82 | -2.979 | 0.32
7/30/2025 21:00 | 19 | 19 | 2.75 | 6.615 | 4.099 | 7.14 | 55 | 1.99 | 68.3 | 0.29 | 0.019 | 46.32 | 10884 | 8.16 | 60 |  | 138 | 3 | 6.8 | -2.979 | 0.32
7/30/2025 21:15 | 19 | 19 | 2.75 | 6.465 | 4.085 | 7.13 | 55 | 1.99 | 68.3 | 0.29 | 0.02 | 46.32 | 10884 | 8.17 | 60 |  | 136.15 | 3.03 | 6.79 | -2.979 | 0.32
7/30/2025 21:30 | 21 | 19 | 2.75 | 6.633 | 3.499 | 7.12 | 55 | 1.99 | 68.3 | 0.29 | 0.019 | 46.32 | 10884 | 8.17 | 60 |  | 137.59 | 2.99 | 6.79 | -2.979 | 0.33
7/30/2025 21:45 | 21 | 19 | 2.75 | 6.675 | 3.252 | 7.11 | 55 | 1.99 | 68.3 | 0.29 | 0.02 | 46.32 | 10884 | 8.17 | 60 |  | 138.45 | 2.99 | 6.79 | -2.979 | 0.32
7/30/2025 22:00 | 21 | 19 | 2.75 | 6.634 | 3.204 | 7.11 | 57 | 1.99 | 68.1 | 0.29 | 0.019 | 46.32 | 10884 | 8.17 | 60 |  | 137.49 | 2.98 | 6.79 | -2.979 | 0.36
7/30/2025 22:15 | 21 | 19 | 2.75 | 6.615 | 3.348 | 7.1 | 57 | 1.99 | 68.1 | 0.29 | 0.019 | 46.32 | 10884 | 8.17 | 60 |  | 137.92 | 3 | 6.78 | -2.979 | 0.31
7/30/2025 22:30 | 17 | 19 | 2.75 | 6.856 | 3.889 | 7.1 | 57 | 1.99 | 68.1 | 0.29 | 0.02 | 46.1 | 10823 | 8.18 | 60 |  | 143.25 | 3.01 | 6.77 | -2.979 | 0.31
7/30/2025 22:45 | 20 | 19 | 2.75 | 6.948 | 3.627 | 7.1 | 57 | 1.99 | 68.1 | 0.29 | 0.02 | 46.1 | 10823 | 8.18 | 60 |  | 143.71 | 2.98 | 6.77 | -2.979 | 0.33
7/30/2025 23:00 | 19 | 19 | 2.75 | 6.135 | 2.998 | 7.1 | 57 | 1.99 | 68.1 | 0.29 | 0.02 | 46.1 | 10823 | 8.19 | 60 |  | 128.51 | 3.02 | 6.78 | -2.979 | 0.34
7/30/2025 23:15 | 20 | 19 | 2.75 | 5.868 | 2.956 | 7.11 | 57 | 1.99 | 68.1 | 0.29 | 0.02 | 46.1 | 10823 | 8.19 | 60 |  | 122.63 | 3.01 | 6.77 | -2.979 | 0.32
7/30/2025 23:30 | 23 | 19 | 2.75 | 6.321 | 3.046 | 7.11 | 57 | 1.99 | 68.1 | 0.29 | 0.02 | 46.1 | 10823 | 8.19 | 60 |  | 131.71 | 3 | 6.77 | -2.979 | 0.31
7/30/2025 23:45 | 23 | 19 | 2.75 | 6.398 | 2.909 | 7.11 | 57 | 1.99 | 68.1 | 0.29 | 0.02 | 46.1 | 10823 | 8.17 | 60 |  | 133.56 | 3.01 | 6.8 | -2.979 | 0.33
7/31/2025 00:00 | 23 | 19 | 2.75 | 6.593 | 3.064 | 7.1 | 57 | 1.99 | 68.1 | 0.296 | 0.02 | 46.1 | 10823 | 8.15 | 60 | 1.52 | 135.95 | 2.97 | 6.84 | -2.979 | 0.33
7/31/2025 00:15 | 22 | 19 | 2.75 | 6.391 | 3.118 | 7.1 | 57 | 1.99 | 68.1 | 0.296 | 0.02 | 46.1 | 10823 | 8.16 | 60 | 1.52 | 134.96 | 3.04 | 6.82 | -2.979 | 0.33
7/31/2025 00:30 | 21 | 19 | 2.75 | 6.57 | 3.065 | 7.1 | 57 | 1.99 | 68.1 | 0.296 | 0.02 | 46.1 | 10823 | 8.19 | 60 | 1.52 | 136.94 | 3 | 6.81 | -2.979 | 0.32
7/31/2025 00:45 | 22 | 19 | 2.75 | 6.435 | 3.132 | 7.1 | 57 | 1.99 | 68.1 | 0.296 | 0.02 | 46.1 | 10823 | 8.22 | 60 | 1.52 | 133.46 | 2.99 | 6.8 | -2.979 | 0.32
7/31/2025 01:00 | 22 | 19 | 2.75 | 6.016 | 3.027 | 7.09 | 57 | 1.99 | 68.1 | 0.296 | 0.02 | 46.1 | 10823 | 8.24 | 60 | 1.52 | 124.81 | 2.99 | 6.78 | -2.979 | 0.32
7/31/2025 01:15 | 22 | 19 | 2.75 | 5.849 | 2.983 | 7.09 | 57 | 1.99 | 68.1 | 0.296 | 0.02 | 46.1 | 10823 | 8.26 | 60 | 1.52 | 122.18 | 3.01 | 6.82 | -2.979 | 0.36
7/31/2025 01:30 | 21 | 19 | 2.75 | 6.302 | 3.128 | 7.09 | 57 | 1.99 | 68.1 | 0.296 | 0.02 | 46.1 | 10823 | 8.26 | 60 | 1.52 | 133.44 | 3.05 | 6.83 | -2.979 | 0.34
7/31/2025 01:45 | 18 | 19 | 2.75 | 6.368 | 3.228 | 7.09 | 57 | 1.99 | 68.1 | 0.296 | 0.019 | 46.1 | 10823 | 8.26 | 60 | 1.52 | 131.93 | 2.98 | 6.82 | -2.979 | 0.33
7/31/2025 02:00 | 20 | 19 | 2.75 | 6.304 | 3.371 | 7.09 | 57 | 1.99 | 68 | 0.296 | 0.02 | 46.1 | 10823 | 8.26 | 59 | 1.52 | 132.14 | 3.02 | 6.81 | -2.979 | 0.32
7/31/2025 02:15 | 19 | 19 | 2.75 | 6.319 | 3.326 | 7.09 | 57 | 1.99 | 68 | 0.296 | 0.02 | 46.1 | 10823 | 8.26 | 59 | 1.52 | 131.88 | 3.01 | 6.83 | -2.979 | 0.31
7/31/2025 02:30 | 22 | 19 | 2.75 | 6.309 | 3.49 | 7.09 | 57 | 1.99 | 68 | 0.296 | 0.019 | 46.1 | 10823 | 8.25 | 59 | 1.52 | 132.92 | 3.03 | 6.82 | -2.979 | 0.32
7/31/2025 02:45 | 21 | 19 | 2.75 | 6.294 | 3.544 | 7.09 | 57 | 1.99 | 68 | 0.296 | 0.019 | 46.1 | 10823 | 8.25 | 59 | 1.52 | 131.73 | 3.01 | 6.83 | -2.979 | 0.3
7/31/2025 03:00 | 19 | 19 | 2.75 | 5.714 | 3.228 | 7.09 | 57 | 1.99 | 68 | 0.296 | 0.019 | 46.1 | 10823 | 8.24 | 59 | 1.52 | 120.03 | 3.02 | 6.83 | -2.979 | 0.31
7/31/2025 03:15 | 19 | 19 | 2.75 | 5.702 | 3.159 | 7.1 | 57 | 1.99 | 68 | 0.296 | 0.019 | 46.1 | 10823 | 8.24 | 59 | 1.52 | 119.16 | 3.01 | 6.8 | -2.979 | 0.3
7/31/2025 03:30 | 21 | 19 | 2.75 | 6.139 | 3.152 | 7.1 | 57 | 1.99 | 68 | 0.296 | 0.019 | 46.1 | 10823 | 8.24 | 59 | 1.52 | 128.09 | 3 | 6.79 | -2.979 | 0.3
7/31/2025 03:45 | 21 | 19 | 2.75 | 5.922 | 3.02 | 7.1 | 57 | 1.99 | 68 | 0.296 | 0.019 | 46.1 | 10823 | 8.23 | 59 | 1.52 | 123.41 | 3 | 6.8 | -2.979 | 0.3
7/31/2025 04:00 | 20 | 19 | 2.75 | 5.932 | 3.103 | 7.1 | 57 | 1.99 | 68 | 0.364 | 0.019 | 46.1 | 10823 | 8.23 | 59 | 1.52 | 158.9 | 3.86 | 6.85 | -2.979 | 0.32
7/31/2025 04:15 | 21 | 19 | 2.75 | 6.443 | 5.353 | 7.09 | 57 | 1.99 | 68 | 0.364 | 0.019 | 46.1 | 10823 | 8.22 | 59 | 1.52 | 179.7 | 4.02 | 6.82 | -2.979 | 0.29
7/31/2025 04:30 | 18 | 19 | 2.75 | 7.871 | 4.212 | 7.09 | 57 | 1.99 | 68 | 0.364 | 0.019 | 46.1 | 10823 | 8.23 | 59 | 1.52 | 181.08 | 3.31 | 6.79 | -2.979 | 0.33
7/31/2025 04:45 | 19 | 19 | 2.75 | 7.903 | 4.083 | 7.08 | 57 | 1.99 | 68 | 0.364 | 0.02 | 46.1 | 10823 | 8.22 | 59 | 1.52 | 180.64 | 3.29 | 6.78 | -2.979 | 0.31
7/31/2025 05:00 | 17 | 19 | 2.75 | 7.961 | 4.003 | 7.08 | 57 | 1.99 | 68 | 0.364 | 0.02 | 46.1 | 10823 | 8.22 | 59 | 1.52 | 180.88 | 3.27 | 6.77 | -2.979 | 0.3
7/31/2025 05:15 | 18 | 19 | 2.75 | 6.046 | 3.844 | 7.08 | 57 | 1.99 | 68 | 0.364 | 0.02 | 46.1 | 10823 | 8.23 | 59 | 1.52 | 167.72 | 3.99 | 6.82 | -2.979 | 0.29
7/31/2025 05:30 | 18 | 19 | 2.75 | 6.651 | 3.518 | 7.08 | 57 | 1.99 | 68 | 0.364 | 0.02 | 45.39 | 10715 | 8.22 | 59 | 1.52 | 181.14 | 3.92 | 6.83 | -2.979 | 0.29
7/31/2025 05:45 | 19 | 19 | 2.75 | 6.649 | 3.397 | 7.08 | 57 | 1.99 | 68 | 0.364 | 0.02 | 45.39 | 10715 | 8.22 | 59 | 1.52 | 180.49 | 3.91 | 6.83 | -2.979 | 0.29
7/31/2025 06:00 | 20 | 19 | 2.75 | 6.784 | 3.219 | 7.09 | 57 | 1.99 | 68 | 0.364 | 0.02 | 45.39 | 10715 | 8.22 | 59 | 1.52 | 180.61 | 3.83 | 6.81 | -2.979 | 0.29
7/31/2025 06:15 | 20 | 19 | 2.75 | 6.781 | 2.998 | 7.09 | 57 | 1.99 | 68 | 0.364 | 0.02 | 45.39 | 10715 | 8.23 | 59 | 1.52 | 180.58 | 3.83 | 6.82 | -2.979 | 0.3
7/31/2025 06:30 | 21 | 19 | 2.75 | 6.78 | 2.997 | 7.09 | 57 | 1.99 | 68 | 0.364 | 0.02 | 45.39 | 10715 | 8.24 | 59 | 1.52 | 180.54 | 3.83 | 6.82 | -2.979 | 0.29
7/31/2025 06:45 | 21 | 19 | 2.75 | 6.96 | 3.174 | 7.1 | 57 | 1.99 | 68 | 0.364 | 0.02 | 45.39 | 10715 | 8.21 | 59 | 1.52 | 181.27 | 3.75 | 6.82 | -2.979 | 0.3
7/31/2025 07:00 | 21 | 19 | 2.75 | 6.404 | 3.031 | 7.09 | 57 | 1.99 | 68 | 0.364 | 0.02 | 45.39 | 10715 | 8.19 | 59 | 1.52 | 178.63 | 4.02 | 6.81 | -2.979 | 0.29
7/31/2025 07:15 | 20 | 19 | 2.75 | 6.114 | 3.236 | 7.09 | 57 | 1.99 | 68 | 0.364 | 0.02 | 45.39 | 10715 | 8.18 | 59 | 1.52 | 169.33 | 3.99 | 6.82 | -2.979 | 0.31
7/31/2025 07:30 | 22 | 19 | 2.75 | 6.643 | 2.994 | 7.08 | 57 | 1.99 | 68 | 0.364 | 0.02 | 45.39 | 10715 | 8.19 | 59 | 1.52 | 180.7 | 3.92 | 6.82 | -2.979 | 0.31
7/31/2025 07:45 | 23 | 19 | 2.75 | 6.738 | 2.995 | 7.09 | 57 | 1.99 | 68 | 0.364 | 0.02 | 45.39 | 10715 | 8.2 | 59 | 1.52 | 180.87 | 3.87 | 6.82 | -2.979 | 0.3
7/31/2025 08:00 | 22 | 19 | 2.75 | 6.613 | 3.033 | 7.09 | 57 | 1.99 | 68 | 0.355 | 0.02 | 45.39 | 10715 | 8.2 | 59 | 1.52 | 180.51 | 3.93 | 6.82 | -2.979 | 0.3
7/31/2025 08:15 | 23 | 19 | 2.75 | 6.823 | 3.126 | 7.09 | 57 | 1.99 | 68 | 0.355 | 0.02 | 45.39 | 10715 | 8.2 | 59 | 1.52 | 180.78 | 3.82 | 6.82 | -2.979 | 0.29
7/31/2025 08:30 | 22 | 19 | 2.75 | 6.646 | 3.194 | 7.09 | 57 | 1.99 | 68 | 0.355 | 0.019 | 45.39 | 10715 | 8.2 | 59 | 1.52 | 180.68 | 3.91 | 6.82 | -2.979 | 0.32
7/31/2025 08:45 | 22 | 19 | 2.75 | 6.764 | 3.31 | 7.1 | 57 | 1.99 | 68 | 0.355 | 0.019 | 45.39 | 10715 | 8.21 | 59 | 1.52 | 180.43 | 3.84 | 6.81 | -2.979 | 0.3
7/31/2025 09:00 | 21 | 19 | 2.75 | 6.668 | 3.194 | 7.1 | 57 | 1.99 | 68 | 0.355 | 0.019 | 45.39 | 10715 | 8.21 | 59 | 1.52 | 180.13 | 3.89 | 6.82 | -2.979 | 0.3
7/31/2025 09:15 | 23 | 19 | 2.75 | 6.675 | 3.133 | 7.1 | 57 | 1.99 | 68 | 0.355 | 0.019 | 45.39 | 10715 | 8.21 | 59 | 1.52 | 180.44 | 3.89 | 6.82 | -2.979 | 0.32
7/31/2025 09:30 | 23 | 19 | 2.75 | 6.684 | 3.175 | 7.1 | 57 | 1.99 | 68 | 0.355 | 0.019 | 45.39 | 10715 | 8.2 | 59 | 1.52 | 180.75 | 3.89 | 6.82 | -2.979 | 0.3
7/31/2025 09:45 | 27 | 19 | 2.75 | 6.68 | 3.089 | 7.1 | 57 | 1.99 | 68 | 0.355 | 0.019 | 45.39 | 10715 | 8.22 | 59 | 1.52 | 180.4 | 3.89 | 6.83 | -2.979 | 0.3
7/31/2025 10:00 | 23 | 19 | 2.75 | 6.643 | 3.108 | 7.1 | 59 | 1.99 | 68 | 0.355 | 0.019 | 45.39 | 10715 | 8.23 | 59 | 1.52 | 180.17 | 3.91 | 6.84 | -2.979 | 0.3
7/31/2025 10:15 | 24 | 19 | 2.75 | 6.179 | 3.305 | 7.1 | 59 | 1.99 | 68 | 0.355 | 0.019 | 45.39 | 10715 | 8.23 | 59 | 1.52 | 172.49 | 4.02 | 6.84 | -2.979 | 0.29
7/31/2025 10:30 | 23 | 19 | 2.75 | 6.555 | 2.992 | 7.1 | 59 | 1.99 | 68 | 0.355 | 0.019 | 45.39 | 10715 | 8.24 | 59 | 1.52 | 180.33 | 3.96 | 6.85 | -2.979 | 0.29
7/31/2025 10:45 | 20 | 19 | 2.75 | 7.116 | 3.025 | 7.1 | 59 | 1.99 | 68 | 0.355 | 0.019 | 45.39 | 10715 | 8.25 | 59 | 1.52 | 181.01 | 3.66 | 6.84 | -2.979 | 0.3
7/31/2025 11:00 | 19 | 19 | 2.75 | 6.918 | 2.999 | 7.1 | 59 | 1.99 | 68 | 0.355 | 0.019 | 45.39 | 10715 | 8.26 | 59 | 1.52 | 181.09 | 3.77 | 6.84 | -2.979 | 0.3
7/31/2025 11:15 | 23 | 19 | 2.75 | 7.496 | 3.125 | 7.1 | 59 | 1.99 | 68 | 0.355 | 0.019 | 45.39 | 10715 | 8.26 | 59 | 1.52 | 180.84 | 3.47 | 6.83 | -2.979 | 0.3
7/31/2025 11:30 | 23 | 19 | 2.75 | 7.55 | 3.722 | 7.15 | 59 | 1.99 | 68 | 0.355 | 0.019 | 45.39 | 10715 | 8.26 | 59 | 1.52 | 180.64 | 3.45 | 6.77 | -2.979 | 0.31
7/31/2025 11:45 | 24 | 19 | 2.75 | 7.573 | 2.187 | 7.1 | 59 | 1.99 | 68 | 0.355 | 0.02 | 45.39 | 10715 | 8.26 | 59 | 1.52 | 180.44 | 3.43 | 6.76 | -2.979 | 0.34
7/31/2025 12:00 | 24 | 19 | 2.75 | 7.862 | 2.414 | 7.12 | 59 | 1.99 | 68 | 0.223 | 0.019 | 45.39 | 10715 | 8.27 | 59 | 1.52 | 180.77 | 3.31 | 6.8 | -3.211 | 0.29
7/31/2025 12:15 | 22 | 19 | 2.75 | 7.881 | 2.307 | 7.12 | 59 | 1.99 | 68 | 0.223 | 0.019 | 45.39 | 10715 | 8.27 | 59 | 1.52 | 180.8 | 3.3 | 6.84 | -3.211 | 0.31
7/31/2025 12:30 | 23 | 19 | 2.75 | 7.864 | 2.134 | 7.13 | 59 | 1.99 | 68 | 0.223 | 0.019 | 45.39 | 10715 | 8.28 | 59 | 1.52 | 180.69 | 3.31 | 6.87 | -3.211 | 0.29
7/31/2025 12:45 | 24 | 19 | 2.75 | 7.833 | 2.03 | 7.13 | 59 | 1.99 | 68 | 0.223 | 0.019 | 45.39 | 10715 | 8.29 | 59 | 1.52 | 180.89 | 3.33 | 6.87 | -3.211 | 0.31
7/31/2025 13:00 | 23 | 19 | 2.75 | 7.879 | 1.936 | 7.13 | 59 | 1.99 | 68 | 0.223 | 0.019 | 45.39 | 10715 | 8.3 | 59 | 1.52 | 181.22 | 3.31 | 6.86 | -3.211 | 0.29
7/31/2025 13:15 | 25 | 19 | 2.75 | 7.842 | 1.902 | 7.13 | 59 | 1.99 | 68 | 0.223 | 0.019 | 45.39 | 10715 | 8.3 | 59 | 1.52 | 181 | 3.32 | 6.86 | -3.211 | 0.3
7/31/2025 13:30 | 26 | 19 | 2.75 | 7.838 | 1.77 | 7.13 | 59 | 1.99 | 68 | 0.223 | 0.019 | 45.39 | 10715 | 8.3 | 59 | 1.52 | 181.26 | 3.33 | 6.86 | -3.211 | 0.37
7/31/2025 13:45 | 27 | 19 | 2.75 | 7.821 | 1.755 | 7.14 | 59 | 1.99 | 68 | 0.223 | 0.019 | 45.39 | 10715 | 8.3 | 59 | 1.52 | 175.62 | 3.23 | 6.86 | -3.211 | 0.28
7/31/2025 14:00 | 20 | 19 | 2.75 | 7.841 | 1.918 | 7.15 | 59 | 1.99 | 68.3 | 0.223 | 0.019 | 45.39 | 10715 | 8.29 | 60 | 1.52 | 178.2 | 3.27 | 6.86 | -3.211 | 0.27
7/31/2025 14:15 | 23 | 19 | 2.75 | 7.777 | 2.201 | 7.15 | 59 | 1.99 | 68.3 | 0.223 | 0.019 | 45.39 | 10715 | 8.28 | 60 | 1.52 | 178.28 | 3.3 | 6.85 | -3.211 | 0.27
7/31/2025 14:30 | 24 | 19 | 2.75 | 7.847 | 2.109 | 7.14 | 59 | 1.99 | 68.3 | 0.223 | 0.019 | 45.39 | 10715 | 8.26 | 60 | 1.52 | 177.97 | 3.27 | 6.85 | -3.211 | 0.28
7/31/2025 14:45 | 24 | 19 | 2.75 | 7.75 | 2.008 | 7.15 | 59 | 1.99 | 68.3 | 0.223 | 0.019 | 45.39 | 10715 | 8.25 | 60 | 1.52 | 178.08 | 3.31 | 6.83 | -3.211 | 0.29
7/31/2025 15:00 | 24 | 19 | 2.75 | 7.749 | 2.019 | 7.15 | 59 | 1.99 | 68.3 | 0.223 | 0.019 | 45.39 | 10715 | 8.24 | 60 | 1.52 | 177.58 | 3.3 | 6.82 | -3.211 | 0.29
7/31/2025 15:15 | 24 | 19 | 2.75 | 7.714 | 1.981 | 7.15 | 59 | 1.99 | 68.3 | 0.223 | 0.019 | 45.39 | 10715 | 8.22 | 60 | 1.52 | 177.48 | 3.31 | 6.82 | -3.211 | 0.28
7/31/2025 15:30 | 25 | 19 | 2.75 | 7.709 | 2.098 | 7.15 | 59 | 1.99 | 68.3 | 0.223 | 0.019 | 45.39 | 10715 | 8.22 | 60 | 1.52 | 177.98 | 3.32 | 6.81 | -3.211 | 0.29
7/31/2025 15:45 | 24 | 19 | 2.75 | 7.681 | 2.302 | 7.15 | 59 | 1.99 | 68.3 | 0.223 | 0.019 | 45.39 | 10715 | 8.21 | 60 | 1.52 | 177.37 | 3.33 | 6.8 | -3.211 | 0.29
7/31/2025 16:00 | 25 | 19 | 2.75 | 7.718 | 2.58 | 7.14 | 59 | 1.99 | 68.3 | 0.247 | 0.019 | 45.39 | 10715 | 8.2 | 60 | 1.52 | 178.09 | 3.32 | 6.78 | -3.211 | 0.28
7/31/2025 16:15 | 22 | 19 | 2.75 | 7.898 | 2.837 | 7.14 | 59 | 1.99 | 68.3 | 0.247 | 0.019 | 45.39 | 10715 | 8.19 | 60 | 1.52 | 110.09 | 2.01 | 6.78 | -3.211 | 0.31
7/31/2025 16:30 | 22 | 19 | 2.75 | 7.925 | 2.893 | 7.15 | 59 | 1.99 | 68.3 | 0.247 | 0.019 | 45.39 | 10715 | 8.19 | 60 | 1.52 | 110.39 | 2.01 | 6.78 | -3.211 | 0.31
7/31/2025 16:45 | 21 | 19 | 2.75 | 7.925 | 2.871 | 7.15 | 59 | 1.99 | 68.3 | 0.247 | 0.019 | 45.39 | 10715 | 8.2 | 60 | 1.52 | 109.88 | 2 | 6.79 | -3.211 | 0.31
7/31/2025 17:00 | 21 | 19 | 2.75 | 7.907 | 2.681 | 7.16 | 59 | 1.99 | 68.3 | 0.247 | 0.019 | 45.39 | 10715 | 8.2 | 60 | 1.52 | 109.94 | 2 | 6.81 | -3.211 | 0.31
7/31/2025 17:15 | 23 | 19 | 2.75 | 7.91 | 3.547 | 7.17 | 59 | 1.99 | 68.3 | 0.247 | 0.019 | 45.39 | 10715 | 8.19 | 60 | 1.52 | 82.91 | 1.51 | 6.82 | -3.211 | 0.3
7/31/2025 17:30 | 23 | 19 | 2.75 | 7.898 | 3.082 | 7.17 | 59 | 1.99 | 68.3 | 0.247 | 0.019 | 45.39 | 10715 | 8.19 | 60 | 1.52 | 82.33 | 1.5 | 6.81 | -3.211 | 0.31
7/31/2025 17:45 | 22 | 19 | 2.75 | 7.937 | 2.87 | 7.18 | 59 | 1.99 | 68.3 | 0.247 | 0.019 | 45.39 | 10715 | 8.19 | 60 | 1.52 | 82.58 | 1.5 | 6.81 | -3.211 | 0.31
7/31/2025 18:00 | 22 | 19 | 2.75 | 7.929 | 3.251 | 7.18 | 59 | 1.99 | 68.1 | 0.247 | 0.019 | 45.39 | 10715 | 8.2 | 60 | 1.52 | 82.59 | 1.5 | 6.79 | -3.211 | 0.3
7/31/2025 18:15 | 23 | 19 | 2.75 | 7.894 | 3.239 | 7.17 | 59 | 1.99 | 68.1 | 0.247 | 0.019 | 45.39 | 10715 | 8.21 | 60 | 1.52 | 82.36 | 1.5 | 6.79 | -3.211 | 0.31
7/31/2025 18:30 | 22 | 19 | 2.75 | 7.861 | 3.151 | 7.17 | 59 | 1.99 | 68.1 | 0.247 | 0.019 | 45.39 | 10715 | 8.21 | 60 | 1.52 | 82.17 | 1.51 | 6.8 | -3.211 | 0.31
7/31/2025 18:45 | 22 | 19 | 2.75 | 7.603 | 3.198 | 7.17 | 59 | 1.99 | 68.1 | 0.247 | 0.019 | 45.39 | 10715 | 8.21 | 60 | 1.52 | 79.62 | 1.51 | 6.8 | -3.211 | 0.31
7/31/2025 19:00 | 21 | 19 | 2.75 | 7.623 | 2.921 | 7.17 | 59 | 1.99 | 68.1 | 0.247 | 0.019 | 45.39 | 10715 | 8.22 | 60 | 1.52 | 78.99 | 1.49 | 6.81 | -3.211 | 0.32
7/31/2025 19:15 | 24 | 19 | 2.75 | 7.732 | 3.016 | 7.18 | 59 | 1.99 | 68.1 | 0.247 | 0.019 | 45.39 | 10715 | 8.22 | 60 | 1.52 | 80.32 | 1.5 | 6.81 | -3.211 | 0.34
7/31/2025 19:30 | 22 | 19 | 2.75 | 7.731 | 3.279 | 7.18 | 59 | 1.99 | 68.1 | 0.247 | 0.019 | 45.39 | 10715 | 8.22 | 60 | 1.52 | 80.39 | 1.5 | 6.8 | -3.211 | 0.32
7/31/2025 19:45 | 23 | 19 | 2.75 | 7.737 | 3.243 | 7.17 | 59 | 1.99 | 68.1 | 0.247 | 0.019 | 45.39 | 10715 | 8.23 | 60 | 1.52 | 80.78 | 1.5 | 6.79 | -3.211 | 0.33
7/31/2025 20:00 | 23 | 19 | 2.75 | 7.755 | 3.242 | 7.17 | 59 | 1.99 | 68.1 | 0.275 | 0.019 | 45.39 | 10715 | 8.23 | 60 | 1.52 | 80.73 | 1.5 | 6.79 | -3.211 | 0.34
7/31/2025 20:15 | 22 | 19 | 2.75 | 7.751 | 3.283 | 7.16 | 59 | 1.99 | 68.1 | 0.275 | 0.019 | 45.39 | 10715 | 8.23 | 60 | 1.52 | 81.18 | 1.51 | 6.78 | -3.211 | 0.33
7/31/2025 20:30 | 25 | 19 | 2.75 | 7.716 | 3.025 | 7.17 | 59 | 1.99 | 68.1 | 0.275 | 0.018 | 45.39 | 10715 | 8.24 | 60 | 1.52 | 80.6 | 1.5 | 6.79 | -3.211 | 0.33
7/31/2025 20:45 | 24 | 19 | 2.75 | 7.733 | 3.003 | 7.17 | 59 | 1.99 | 68.1 | 0.275 | 0.019 | 45.39 | 10715 | 8.24 | 60 | 1.52 | 80.74 | 1.5 | 6.8 | -3.211 | 0.32
7/31/2025 21:00 | 23 | 19 | 2.75 | 7.778 | 3.006 | 7.17 | 59 | 1.99 | 68.1 | 0.275 | 0.018 | 45.39 | 10715 | 8.24 | 60 | 1.52 | 80.72 | 1.49 | 6.79 | -3.211 | 0.33
7/31/2025 21:15 | 24 | 19 | 2.75 | 7.754 | 3.235 | 7.17 | 59 | 1.99 | 68.1 | 0.275 | 0.018 | 45.39 | 10715 | 8.23 | 60 | 1.52 | 80.83 | 1.5 | 6.79 | -3.211 | 0.33
7/31/2025 21:30 | 23 | 19 | 2.75 | 7.408 | 3.297 | 7.16 | 59 | 1.99 | 68.1 | 0.275 | 0.018 | 45.39 | 10715 | 8.24 | 60 | 1.52 | 77.8 | 1.51 | 6.78 | -3.211 | 0.34
7/31/2025 21:45 | 23 | 19 | 2.75 | 7.359 | 3.413 | 7.15 | 59 | 1.99 | 68.1 | 0.275 | 0.018 | 45.39 | 10715 | 8.24 | 60 | 1.52 | 77.5 | 1.52 | 6.78 | -3.211 | 0.36
7/31/2025 22:00 | 23 | 19 | 2.75 | 7.675 | 3.389 | 7.15 | 59 | 1.99 | 68.1 | 0.275 | 0.018 | 45.39 | 10715 | 8.25 | 60 | 1.52 | 79.54 | 1.49 | 6.78 | -3.211 | 0.33
7/31/2025 22:15 | 23 | 19 | 2.75 | 7.722 | 2.917 | 7.16 | 59 | 1.99 | 68.1 | 0.275 | 0.018 | 45.39 | 10715 | 8.25 | 60 | 1.52 | 79.77 | 1.49 | 6.79 | -3.211 | 0.34
7/31/2025 22:30 | 23 | 19 | 2.75 | 7.702 | 2.69 | 7.18 | 59 | 1.99 | 68.1 | 0.275 | 0.018 | 45.39 | 10715 | 8.25 | 60 | 1.52 | 80.2 | 1.5 | 6.8 | -3.211 | 0.32
7/31/2025 22:45 | 24 | 19 | 2.75 | 7.66 | 2.712 | 7.19 | 59 | 1.99 | 68.1 | 0.275 | 0.018 | 45.39 | 10715 | 8.25 | 60 | 1.52 | 79.95 | 1.5 | 6.81 | -3.211 | 0.32
7/31/2025 23:00 | 25 | 19 | 2.75 | 7.712 | 2.868 | 7.2 | 59 | 1.99 | 68.1 | 0.275 | 0.018 | 45.39 | 10715 | 8.25 | 60 | 1.52 | 107.74 | 2.01 | 6.81 | -3.211 | 0.3
7/31/2025 23:15 | 25 | 19 | 2.75 | 7.359 | 2.368 | 7.21 | 59 | 1.99 | 68.1 | 0.275 | 0.018 | 45.39 | 10715 | 8.26 | 60 | 1.52 | 81.98 | 1.6 | 6.83 | -3.211 | 0.31
7/31/2025 23:30 | 23 | 19 | 2.75 | 7.27 | 2.538 | 7.22 | 59 | 1.99 | 68.1 | 0.275 | 0.018 | 45.39 | 10715 | 8.26 | 60 | 1.52 | 101.4 | 2.01 | 6.86 | -3.211 | 0.3
7/31/2025 23:45 | 23 | 19 | 2.75 | 7.596 | 3.951 | 7.19 | 59 | 1.99 | 68.1 | 0.275 | 0.018 | 45.39 | 10715 | 8.27 | 60 | 1.52 | 104.17 | 1.97 | 6.8 | -3.211 | 0.31
8/1/2025 00:00 | 21 | 19 | 2.75 | 7.51 | 3.879 | 7.17 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.27 | 60 | 1.63 | 104.5 | 2 | 6.79 | -3.211 | 0.3
8/1/2025 00:15 | 12 | 19 | 2.75 | 7.454 | 3.767 | 7.16 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.27 | 60 | 1.63 | 104.37 | 2.02 | 6.78 | -3.211 | 0.32
8/1/2025 00:30 | 17 | 19 | 2.75 | 7.63 | 3.794 | 7.15 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.27 | 60 | 1.63 | 105.27 | 1.99 | 6.78 | -3.211 | 0.32
8/1/2025 00:45 | 18 | 19 | 2.75 | 7.5 | 3.822 | 7.15 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.27 | 60 | 1.63 | 104.77 | 2.01 | 6.78 | -3.211 | 0.32
8/1/2025 01:00 | 20 | 19 | 2.75 | 7.542 | 4.208 | 7.14 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.27 | 60 | 1.63 | 104.77 | 2 | 6.77 | -3.211 | 0.32
8/1/2025 01:15 | 19 | 19 | 2.75 | 7.566 | 4.511 | 7.14 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.27 | 60 | 1.63 | 104.85 | 2 | 6.78 | -3.211 | 0.33
8/1/2025 01:30 | 18 | 19 | 2.75 | 7.508 | 4.432 | 7.13 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.27 | 60 | 1.63 | 104.42 | 2 | 6.78 | -3.211 | 0.31
8/1/2025 01:45 | 17 | 19 | 2.75 | 6.932 | 4.168 | 7.14 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.26 | 60 | 1.63 | 98.35 | 2.04 | 6.78 | -3.211 | 0.34
8/1/2025 02:00 | 18 | 19 | 2.75 | 6.924 | 3.814 | 7.14 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.26 | 60 | 1.63 | 95.99 | 2 | 6.81 | -3.211 | 0.32
8/1/2025 02:15 | 16 | 19 | 2.75 | 7.321 | 3.996 | 7.15 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.26 | 60 | 1.63 | 103.41 | 2.03 | 6.81 | -3.211 | 0.35
8/1/2025 02:30 | 19 | 19 | 2.75 | 7.305 | 3.777 | 7.14 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.26 | 60 | 1.63 | 100.94 | 1.99 | 6.79 | -3.211 | 0.34
8/1/2025 02:45 | 15 | 19 | 2.75 | 7.399 | 3.661 | 7.14 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.26 | 60 | 1.63 | 100.37 | 1.95 | 6.79 | -3.211 | 0.35
8/1/2025 03:00 | 16 | 19 | 2.75 | 7.392 | 3.554 | 7.14 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.27 | 60 | 1.63 | 101.98 | 1.99 | 6.79 | -3.211 | 0.34
8/1/2025 03:15 | 15 | 19 | 2.75 | 7.282 | 3.378 | 7.15 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.27 | 60 | 1.63 | 102.04 | 2.02 | 6.79 | -3.211 | 0.34
8/1/2025 03:30 | 19 | 19 | 2.75 | 6.618 | 3.35 | 7.16 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.28 | 60 | 1.63 | 91.16 | 1.98 | 6.82 | -3.211 | 0.32
8/1/2025 03:45 | 21 | 19 | 2.75 | 6.493 | 3.477 | 7.15 | 59 | 1.96 | 68.1 | 0.305 | 0.018 | 45.39 | 10715 | 8.28 | 60 | 1.63 | 90.36 | 2 | 6.81 | -3.211 | 0.32
8/1/2025 04:00 | 15 | 19 | 2.75 | 7.127 | 3.393 | 7.14 | 59 | 1.96 | 68.1 | 0.423 | 0.018 | 45.39 | 10715 | 8.28 | 60 | 1.63 | 98.08 | 1.98 | 6.8 | -3.211 | 0.33
8/1/2025 04:15 | 18 | 19 | 2.75 | 7.088 | 4.029 | 7.12 | 59 | 1.96 | 68.1 | 0.423 | 0.018 | 45.39 | 10715 | 8.28 | 60 | 1.63 | 98.44 | 2 | 6.77 | -3.211 | 0.33
8/1/2025 04:30 | 19 | 19 | 2.75 | 7.022 | 4.297 | 7.11 | 59 | 1.96 | 68.1 | 0.423 | 0.018 | 45.39 | 10715 | 8.28 | 60 | 1.63 | 98.41 | 2.02 | 6.76 | -3.211 | 0.33
8/1/2025 04:45 | 14 | 19 | 2.75 | 7.011 | 4.412 | 7.11 | 59 | 1.96 | 68.1 | 0.423 | 0.018 | 45.39 | 10715 | 8.28 | 60 | 1.63 | 98.69 | 2.03 | 6.75 | -3.211 | 0.31
8/1/2025 05:00 | 13 | 19 | 2.75 | 6.631 | 4.336 | 7.11 | 59 | 1.96 | 68.1 | 0.423 | 0.018 | 45.39 | 10715 | 8.28 | 60 | 1.63 | 91.07 | 1.98 | 6.77 | -3.211 | 0.32
8/1/2025 05:15 | 14 | 19 | 2.75 | 8.277 | 4.328 | 7.11 | 59 | 1.96 | 68.1 | 0.423 | 0.018 | 45.39 | 10715 | 8.27 | 60 | 1.63 | 87.02 | 1.51 | 6.77 | -3.211 | 0.32
8/1/2025 05:30 | 14 | 19 | 2.75 | 6.751 | 4.198 | 7.12 | 59 | 1.96 | 68.1 | 0.423 | 0.018 | 45.39 | 10715 | 8.27 | 60 | 1.63 | 70.59 | 1.51 | 6.76 | -3.211 | 0.33
8/1/2025 05:45 | 16 | 19 | 2.75 | 7.357 | 4.037 | 7.12 | 59 | 1.96 | 68.1 | 0.423 | 0.019 | 44.81 | 10568 | 8.26 | 60 | 1.63 | 76.72 | 1.5 | 6.8 | -3.211 | 0.33
8/1/2025 06:00 | 21 | 19 | 2.75 | 7.457 | 3.796 | 7.13 | 59 | 1.96 | 68 | 0.423 | 0.019 | 44.81 | 10568 | 8.26 | 60 | 1.63 | 77.05 | 1.49 | 6.8 | -3.211 | 0.32
8/1/2025 06:15 | 18 | 19 | 2.75 | 7.358 | 3.859 | 7.14 | 59 | 1.96 | 68 | 0.423 | 0.019 | 44.81 | 10568 | 8.26 | 60 | 1.63 | 77.1 | 1.51 | 6.8 | -3.211 | 0.3
8/1/2025 06:30 | 19 | 19 | 2.75 | 7.364 | 4.076 | 7.15 | 59 | 1.96 | 68 | 0.423 | 0.019 | 44.81 | 10568 | 8.24 | 60 | 1.63 | 77.31 | 1.51 | 6.8 | -3.211 | 0.3
8/1/2025 06:45 | 16 | 19 | 2.75 | 8.244 | 4.088 | 7.15 | 59 | 1.96 | 68 | 0.423 | 0.019 | 44.81 | 10568 | 8.23 | 60 | 1.63 | 85.65 | 1.5 | 6.79 | -3.211 | 0.3
8/1/2025 07:00 | 18 | 19 | 2.75 | 8.256 | 3.973 | 7.15 | 59 | 1.96 | 68 | 0.423 | 0.019 | 44.81 | 10568 | 8.21 | 60 | 1.63 | 86.29 | 1.51 | 6.79 | -3.211 | 0.3
8/1/2025 07:15 | 18 | 19 | 2.75 | 8.256 | 3.912 | 7.15 | 59 | 1.96 | 68 | 0.423 | 0.02 | 44.81 | 10568 | 8.2 | 60 | 1.63 | 86.15 | 1.5 | 6.78 | -3.211 | 0.32
8/1/2025 07:30 | 21 | 19 | 2.75 | 8.169 | 4.01 | 7.15 | 59 | 1.96 | 68 | 0.423 | 0.019 | 44.81 | 10568 | 8.21 | 60 | 1.63 | 85.31 | 1.5 | 6.79 | -3.211 | 0.3
8/1/2025 07:45 | 19 | 19 | 2.75 | 7.888 | 4.092 | 7.16 | 59 | 1.96 | 68 | 0.423 | 0.019 | 44.81 | 10568 | 8.23 | 60 | 1.63 | 82.71 | 1.51 | 6.8 | -3.211 | 0.32
8/1/2025 08:00 | 21 | 19 | 2.75 | 8.049 | 4.151 | 7.16 | 59 | 1.96 | 68 | 0.39 | 0.019 | 44.81 | 10568 | 8.23 | 60 | 1.63 | 79.38 | 1.42 | 6.8 | -3.211 | 0.32
8/1/2025 08:15 | 20 | 19 | 2.75 | 8.11 | 4.29 | 7.16 | 59 | 1.96 | 68 | 0.39 | 0.019 | 44.81 | 10568 | 8.24 | 60 | 1.63 | 84.54 | 1.5 | 6.81 | -3.211 | 0.31
8/1/2025 08:30 | 20 | 19 | 2.75 | 8.098 | 39.937 | 7.15 | 59 | 1.96 | 68 | 0.39 | 0.019 | 44.81 | 10568 | 8.25 | 60 | 1.63 | 84.36 | 1.5 | 6.8 | -3.211 | 0.26
8/1/2025 08:45 | 19 | 19 | 2.75 | 8.112 | 6.879 | 7.13 | 59 | 1.96 | 68 | 0.39 | 0.019 | 44.81 | 10568 | 8.26 | 60 | 1.63 | 84.72 | 1.5 | 6.75 | -3.211 | 0.3
8/1/2025 09:00 | 10 | 19 | 2.75 | 8.102 | 3.411 | 7.14 | 59 | 1.96 | 68 | 0.39 | 0.019 | 44.81 | 10568 | 8.25 | 60 | 1.63 | 84.4 | 1.5 | 6.76 | -3.211 | 0.29
8/1/2025 09:15 | 18 | 19 | 2.75 | 8.126 | 3.138 | 7.15 | 59 | 1.96 | 68 | 0.39 | 0.019 | 44.81 | 10568 | 8.25 | 60 | 1.63 | 84.53 | 1.5 | 6.81 | -3.211 | 0.29
8/1/2025 09:30 | 20 | 19 | 2.75 | 8.099 | 3.241 | 7.15 | 59 | 1.96 | 68 | 0.39 | 0.019 | 44.81 | 10568 | 8.25 | 60 | 1.63 | 84.58 | 1.5 | 6.84 | -3.211 | 0.3
8/1/2025 09:45 | 22 | 19 | 2.75 | 8.088 | 3.355 | 7.15 | 59 | 1.96 | 68 | 0.39 | 0.019 | 44.81 | 10568 | 8.17 | 60 | 1.63 | 84.78 | 1.51 | 6.84 | -3.211 | 0.29
8/1/2025 10:00 | 18 | 19 | 2.75 | 8.102 | 3.407 | 7.15 | 58 | 1.96 | 68 | 0.39 | 0.019 | 44.81 | 10568 | 8.19 | 60 | 1.63 | 84.58 | 1.5 | 6.83 | -3.211 | 0.29
8/1/2025 10:15 | 20 | 19 | 2.75 | 8.137 | 2.258 | 7.15 | 58 | 1.96 | 68 | 0.39 | 0.019 | 44.81 | 10568 | 8.23 | 60 | 1.63 | 84.75 | 1.5 | 6.83 | -3.211 | 0.3
8/1/2025 10:30 | 18 | 19 | 2.75 | 8.115 | 3.163 | 7.12 | 58 | 1.96 | 68 | 0.39 | 0.018 | 44.81 | 10568 | 8.24 | 60 | 1.63 | 85.2 | 1.51 | 6.82 | -3.211 | 0.3
8/1/2025 10:45 | 19 | 19 | 2.75 | 8.123 | 3.046 | 7.1 | 58 | 1.96 | 68 | 0.39 | 0.019 | 44.81 | 10568 | 8.27 | 60 | 1.63 | 85.15 | 1.51 | 6.81 | -3.211 | 0.3
8/1/2025 11:00 | 19 | 19 | 2.75 | 8.134 | 2.997 | 7.11 | 58 | 1.96 | 68 | 0.39 | 0.019 | 44.81 | 10568 | 8.28 | 60 | 1.63 | 85.03 | 1.51 | 6.81 | -3.211 | 0.31
8/1/2025 11:15 | 18 | 19 | 2.75 | 8.117 | 2.987 | 7.13 | 58 | 1.96 | 68 | 0.39 | 0.019 | 44.81 | 10568 | 8.29 | 60 | 1.63 | 85.07 | 1.51 | 6.82 | -3.211 | 0.31
8/1/2025 11:30 | 20 | 19 | 2.75 | 8.147 | 2.971 | 7.13 | 58 | 1.96 | 68 | 0.39 | 0.018 | 44.81 | 10568 | 8.29 | 60 | 1.63 | 83.9 | 1.48 | 6.82 | -3.211 | 0.32
8/1/2025 11:45 | 20 | 19 | 2.75 | 7.713 | 3.016 | 7.13 | 58 | 1.96 | 68 | 0.39 | 0.018 | 44.81 | 10568 | 8.29 | 60 | 1.63 | 80.75 | 1.51 | 6.82 | -3.211 | 0.29
8/1/2025 12:00 | 21 | 19 | 2.75 | 8.042 | 2.959 | 7.14 | 58 | 1.96 | 68 | 0.237 | 0.018 | 44.81 | 10568 | 8.29 | 60 | 1.63 | 84.2 | 1.51 | 6.83 | -3.211 | 0.3
8/1/2025 12:15 | 20 | 19 | 2.75 | 8.339 | 2.995 | 7.14 | 58 | 1.96 | 68 | 0.237 | 0.018 | 44.81 | 10568 | 8.28 | 60 | 1.63 | 86.93 | 1.5 | 6.82 | -3.211 | 0.31
8/1/2025 12:30 | 20 | 19 | 2.75 | 8.284 | 2.906 | 7.14 | 58 | 1.96 | 68 | 0.237 | 0.018 | 44.81 | 10568 | 8.27 | 60 | 1.63 | 86.9 | 1.51 | 6.82 | -3.211 | 0.33
8/1/2025 12:45 | 22 | 19 | 2.75 | 7.062 | 2.812 | 7.14 | 58 | 1.96 | 68 | 0.237 | 0.018 | 44.81 | 10568 | 8.26 | 60 | 1.63 | 74.05 | 1.51 | 6.82 | -3.211 | 0.28
8/1/2025 13:00 | 23 | 19 | 2.75 | 7.355 | 2.746 | 7.15 | 58 | 1.96 | 68 | 0.237 | 0.018 | 44.81 | 10568 | 8.25 | 60 | 1.63 | 76.32 | 1.49 | 6.83 | -3.211 | 0.31
8/1/2025 13:15 | 25 | 19 | 2.75 | 7.656 | 2.808 | 7.15 | 58 | 1.96 | 68 | 0.237 | 0.018 | 45.84 | 10738 | 8.24 | 60 | 1.63 | 79.04 | 1.49 | 6.83 | -3.211 | 0.31
8/1/2025 13:30 | 23 | 19 | 2.75 | 7.576 | 2.72 | 7.16 | 58 | 1.96 | 68 | 0.237 | 0.018 | 45.84 | 10738 | 8.23 | 60 | 1.63 | 79.29 | 1.51 | 6.8 | -3.211 | 0.31
8/1/2025 13:45 | 24 | 19 | 2.75 | 7.354 | 3.186 | 7.16 | 58 | 1.96 | 68 | 0.237 | 0.019 | 45.84 | 10738 | 8.23 | 60 | 1.63 | 77.06 | 1.51 | 6.85 | -3.211 | 0.32
8/1/2025 14:00 | -1 | 19 | 2.75 | 6.926 | 2.764 | 7.17 | 58 | 1.96 | 68 | 0.237 | 0.019 | 45.84 | 10738 | 8.22 | 61 | 1.63 | 72.14 | 1.5 | 6.82 | -3.211 | 0.31
8/1/2025 14:15 | 15 | 19 | 2.75 | 6.909 | 2.667 | 7.17 | 58 | 1.96 | 68 | 0.237 | 0.019 | 45.84 | 10738 | 8.21 | 61 | 1.63 | 72.26 | 1.51 | 6.83 | -3.211 | 0.32
8/1/2025 14:30 | 20 | 19 | 2.75 | 7.609 | 3.625 | 7.16 | 58 | 1.96 | 68 | 0.237 | 0.019 | 45.84 | 10738 | 8.18 | 61 | 1.63 | 79.69 | 1.51 | 6.81 | -3.211 | 0.28
8/1/2025 14:45 | 22 | 19 | 2.75 | 7.643 | 3.638 | 7.16 | 58 | 1.96 | 68 | 0.237 | 0.019 | 45.84 | 10738 | 8.15 | 61 | 1.63 | 79.66 | 1.5 | 6.79 | -3.211 | 0.29
8/1/2025 15:00 | 21 | 19 | 2.75 | 7.525 | 3.67 | 7.15 | 58 | 1.96 | 68 | 0.237 | 0.019 | 45.84 | 10738 | 8.16 | 61 | 1.63 | 79.48 | 1.52 | 6.78 | -3.211 | 0.3
8/1/2025 15:15 | 23 | 19 | 2.75 | 6.949 | 4.039 | 7.14 | 58 | 1.96 | 68 | 0.237 | 0.019 | 45.84 | 10738 | 8.19 | 61 | 1.63 | 73.06 | 1.51 | 6.78 | -3.211 | 0.3
8/1/2025 15:30 | 24 | 19 | 2.75 | 7.052 | 4.225 | 7.14 | 58 | 1.96 | 68 | 0.237 | 0.019 | 45.84 | 10738 | 8.23 | 61 | 1.63 | 73.06 | 1.49 | 6.78 | -3.211 | 0.29
8/1/2025 15:45 | 23 | 19 | 2.75 | 7.566 | 4.366 | 7.14 | 58 | 1.96 | 68 | 0.237 | 0.019 | 45.84 | 10738 | 8.27 | 61 | 1.63 | 79.09 | 1.51 | 6.78 | -3.211 | 0.3
8/1/2025 16:00 | 22 | 19 | 2.75 | 7.555 | 4.101 | 7.15 | 58 | 1.96 | 68 | 0.266 | 0.018 | 45.84 | 10738 | 8.3 | 61 | 1.63 | 79.3 | 1.51 | 6.78 | -3.211 | 0.31
8/1/2025 16:15 | 23 | 19 | 2.75 | 7.579 | 3.874 | 7.16 | 58 | 1.96 | 68 | 0.266 | 0.018 | 45.84 | 10738 | 8.31 | 61 | 1.63 | 78.57 | 1.49 | 6.79 | -3.211 | 0.31
8/1/2025 16:30 | 24 | 19 | 2.75 | 6.941 | 3.589 | 7.16 | 58 | 1.96 | 68 | 0.266 | 0.018 | 45.84 | 10738 | 8.32 | 61 | 1.63 | 72.64 | 1.51 | 6.81 | -3.211 | 0.3
8/1/2025 16:45 | 26 | 19 | 2.75 | 7.158 | 3.584 | 7.16 | 58 | 1.96 | 68 | 0.266 | 0.018 | 45.84 | 10738 | 8.33 | 61 | 1.63 | 73.49 | 1.48 | 6.81 | -3.211 | 0.31
8/1/2025 17:00 | 25 | 19 | 2.75 | 7.614 | 3.628 | 7.16 | 58 | 1.96 | 68 | 0.266 | 0.018 | 45.84 | 10738 | 8.33 | 61 | 1.63 | 78.78 | 1.49 | 6.8 | -3.211 | 0.31
8/1/2025 17:15 | 26 | 19 | 2.75 | 7.604 | 3.514 | 7.16 | 58 | 1.96 | 68 | 0.266 | 0.019 | 45.89 | 10788 | 8.32 | 61 | 1.63 | 78.82 | 1.49 | 6.79 | -3.211 | 0.32
8/1/2025 17:30 | 30 | 19 | 2.75 | 7.52 | 3.393 | 7.15 | 58 | 1.96 | 68 | 0.266 | 0.02 | 45.89 | 10788 | 8.31 | 61 | 1.63 | 77.66 | 1.49 | 6.78 | -3.211 | 0.31
8/1/2025 17:45 | 29 | 19 | 2.75 | 7.072 | 3.306 | 7.18 | 58 | 1.96 | 68 | 0.266 | 0.019 | 45.89 | 10788 | 8.29 | 61 | 1.63 | 73.98 | 1.51 | 6.82 | -3.211 | 0.31
8/1/2025 18:00 | 28 | 19 | 2.75 | 7.184 | 3.744 | 7.15 | 58 | 1.96 | 68.1 | 0.266 | 0.019 | 45.89 | 10788 | 8.29 | 61 | 1.63 | 74.2 | 1.49 | 6.8 | -3.211 | 0.31
8/1/2025 18:15 | 25 | 19 | 2.75 | 7.512 | 3.828 | 7.15 | 58 | 1.96 | 68.1 | 0.266 | 0.019 | 45.89 | 10788 | 8.27 | 61 | 1.63 | 78.4 | 1.5 | 6.78 | -3.211 | 0.32
8/1/2025 18:30 | 27 | 19 | 2.75 | 7.46 | 3.753 | 7.15 | 58 | 1.96 | 68.1 | 0.266 | 0.019 | 45.89 | 10788 | 8.26 | 61 | 1.63 | 78.24 | 1.51 | 6.78 | -3.211 | 0.32
8/1/2025 18:45 | 28 | 19 | 2.75 | 6.542 | 3.554 | 7.16 | 58 | 1.96 | 68.1 | 0.266 | 0.019 | 45.89 | 10788 | 8.28 | 61 | 1.63 | 67.5 | 1.49 | 6.79 | -3.211 | 0.32
8/1/2025 19:00 | 28 | 19 | 2.75 | 6.401 | 3.751 | 7.15 | 58 | 1.96 | 68.1 | 0.266 | 0.019 | 45.89 | 10788 | 8.3 | 61 | 1.63 | 67.63 | 1.52 | 6.8 | -3.211 | 0.32
8/1/2025 19:15 | 30 | 19 | 2.75 | 6.962 | 5.526 | 7.13 | 58 | 1.96 | 68.1 | 0.266 | 0.019 | 45.89 | 10788 | 8.32 | 61 | 1.63 | 72.9 | 1.51 | 6.78 | -3.211 | 0.31
8/1/2025 19:30 | 28 | 19 | 2.75 | 7.075 | 5.256 | 7.12 | 58 | 1.96 | 68.1 | 0.266 | 0.019 | 45.89 | 10788 | 8.33 | 61 | 1.63 | 73.05 | 1.49 | 6.76 | -3.211 | 0.3
8/1/2025 19:45 | 22 | 19 | 2.75 | 6.89 | 5.683 | 7.11 | 58 | 1.96 | 68.1 | 0.266 | 0.019 | 45.89 | 10788 | 8.33 | 61 | 1.63 | 72.88 | 1.52 | 6.75 | -3.211 | 0.3
8/1/2025 20:00 | 23 | 19 | 2.75 | 6.916 | 5.505 | 7.1 | 58 | 1.96 | 68.1 | 0.28 | 0.019 | 45.89 | 10788 | 8.32 | 61 | 1.63 | 72.42 | 1.51 | 6.74 | -3.211 | 0.3
8/1/2025 20:15 | 23 | 19 | 2.75 | 6.718 | 5.343 | 7.09 | 58 | 1.96 | 68.1 | 0.28 | 0.019 | 45.89 | 10788 | 8.31 | 61 | 1.63 | 139.67 | 2.99 | 6.74 | -3.211 | 0.3
8/1/2025 20:30 | 23 | 19 | 2.75 | 6.756 | 5.225 | 7.08 | 58 | 1.96 | 68.1 | 0.28 | 0.019 | 45.89 | 10788 | 8.3 | 61 | 1.63 | 139.81 | 2.98 | 6.74 | -3.211 | 0.3
8/1/2025 20:45 | 23 | 19 | 2.75 | 6.806 | 5.223 | 7.08 | 58 | 1.96 | 68.1 | 0.28 | 0.019 | 45.89 | 10788 | 8.29 | 61 | 1.63 | 143.77 | 3.04 | 6.75 | -3.211 | 0.32
8/1/2025 21:00 | 23 | 19 | 2.75 | 7.031 | 4.662 | 7.09 | 58 | 1.96 | 68.1 | 0.28 | 0.019 | 45.89 | 10788 | 8.28 | 61 | 1.63 | 145.5 | 2.98 | 6.76 | -3.211 | 0.32
8/1/2025 21:15 | 23 | 19 | 2.75 | 7.156 | 4.529 | 7.09 | 58 | 1.96 | 68.1 | 0.28 | 0.019 | 45.89 | 10788 | 8.28 | 61 | 1.63 | 149.86 | 3.02 | 6.76 | -3.211 | 0.33
8/1/2025 21:30 | 24 | 19 | 2.75 | 7.231 | 3.966 | 7.09 | 58 | 1.96 | 68.1 | 0.28 | 0.019 | 45.89 | 10788 | 8.28 | 61 | 1.63 | 149.88 | 2.98 | 6.77 | -3.211 | 0.32
8/1/2025 21:45 | 29 | 19 | 2.75 | 7.3 | 3.725 | 7.09 | 58 | 1.96 | 68.1 | 0.28 | 0.019 | 45.89 | 10788 | 8.28 | 61 | 1.63 | 151.02 | 2.98 | 6.78 | -3.211 | 0.33
8/1/2025 22:00 | 28 | 19 | 2.75 | 6.937 | 3.592 | 7.09 | 57 | 1.96 | 68 | 0.28 | 0.019 | 45.89 | 10788 | 8.28 | 61 | 1.63 | 144.55 | 3 | 6.78 | -3.211 | 0.32
8/1/2025 22:15 | 26 | 19 | 2.75 | 6.909 | 3.509 | 7.09 | 57 | 1.96 | 68 | 0.28 | 0.019 | 45.89 | 10788 | 8.28 | 61 | 1.63 | 144.33 | 3.01 | 6.78 | -3.211 | 0.32
8/1/2025 22:30 | 22 | 19 | 2.75 | 7.053 | 3.861 | 7.09 | 57 | 1.96 | 68 | 0.28 | 0.019 | 45.89 | 10788 | 8.27 | 61 | 1.63 | 147.51 | 3.01 | 6.77 | -3.211 | 0.34
8/1/2025 22:45 | 26 | 19 | 2.75 | 7.088 | 3.716 | 7.08 | 57 | 1.96 | 68 | 0.28 | 0.019 | 45.89 | 10788 | 8.26 | 61 | 1.63 | 147.2 | 2.99 | 6.76 | -3.211 | 0.32
8/1/2025 23:00 | 25 | 19 | 2.75 | 7.03 | 3.698 | 7.08 | 57 | 1.96 | 68 | 0.28 | 0.019 | 45.89 | 10788 | 8.26 | 61 | 1.63 | 147.01 | 3.01 | 6.75 | -3.211 | 0.31
8/1/2025 23:15 | 23 | 19 | 2.75 | 7.047 | 3.595 | 7.08 | 57 | 1.96 | 68 | 0.28 | 0.019 | 45.89 | 10788 | 8.25 | 61 | 1.63 | 147.62 | 3.02 | 6.75 | -3.211 | 0.33
8/1/2025 23:30 | 23 | 19 | 2.75 | 7.226 | 3.543 | 7.09 | 57 | 1.96 | 68 | 0.28 | 0.019 | 45.89 | 10788 | 8.25 | 61 | 1.63 | 150.43 | 3 | 6.76 | -3.211 | 0.32
8/1/2025 23:45 | 25 | 19 | 2.75 | 7.176 | 3.686 | 7.09 | 57 | 1.96 | 68 | 0.28 | 0.019 | 45.89 | 10788 | 8.24 | 61 | 1.63 | 150.37 | 3.02 | 6.76 | -3.211 | 0.32
8/2/2025 00:00 | 27 | 19 | 2.75 | 6.747 | 3.188 | 7.09 | 57 | 1.93 | 68 | 0.343 | 0.019 | 45.89 | 10788 | 8.23 | 61 |  | 139.8 | 2.98 | 6.76 | -3.211 | 0.33
8/2/2025 00:15 | 26 | 19 | 2.75 | 6.514 | 3.245 | 7.09 | 57 | 1.93 | 68 | 0.343 | 0.019 | 45.89 | 10788 | 8.22 | 61 |  | 135.27 | 2.99 | 6.79 | -3.211 | 0.33
8/2/2025 00:30 | 23 | 19 | 2.75 | 7.109 | 3.597 | 7.1 | 57 | 1.93 | 68 | 0.343 | 0.019 | 45.89 | 10788 | 8.22 | 61 |  | 148.53 | 3.01 | 6.78 | -3.211 | 0.32
8/2/2025 00:45 | 25 | 19 | 2.75 | 7.122 | 2.835 | 7.11 | 57 | 1.93 | 68 | 0.343 | 0.019 | 45.89 | 10788 | 8.21 | 61 |  | 173.59 | 3.51 | 6.77 | -3.211 | 0.32
8/2/2025 01:00 | 23 | 19 | 2.75 | 7.122 | 2.676 | 7.13 | 57 | 1.93 | 68 | 0.343 | 0.019 | 45.89 | 10788 | 8.21 | 61 |  | 172.94 | 3.5 | 6.79 | -3.211 | 0.3
8/2/2025 01:15 | 26 | 19 | 2.75 | 7.127 | 3.011 | 7.13 | 57 | 1.93 | 68 | 0.343 | 0.019 | 45.89 | 10788 | 8.21 | 61 |  | 173.62 | 3.51 | 6.8 | -3.211 | 0.3
8/2/2025 01:30 | 26 | 19 | 2.75 | 7.118 | 3.02 | 7.13 | 57 | 1.93 | 68 | 0.343 | 0.019 | 45.89 | 10788 | 8.2 | 61 |  | 173.26 | 3.51 | 6.8 | -3.211 | 0.33
8/2/2025 01:45 | 23 | 19 | 2.75 | 6.923 | 3.835 | 7.1 | 57 | 1.93 | 68 | 0.343 | 0.019 | 45.89 | 10788 | 8.2 | 61 |  | 168.09 | 3.5 | 6.79 | -3.211 | 0.29
8/2/2025 02:00 | 22 | 19 | 2.75 | 6.9 | 3.948 | 7.08 | 57 | 1.93 | 68 | 0.343 | 0.019 | 45.89 | 10788 | 8.2 | 61 |  | 168.14 | 3.51 | 6.77 | -3.211 | 0.3
8/2/2025 02:15 | 21 | 19 | 2.75 | 6.923 | 4.116 | 7.07 | 57 | 1.93 | 68 | 0.343 | 0.019 | 45.89 | 10788 | 8.19 | 61 |  | 168.65 | 3.51 | 6.76 | -3.211 | 0.29
8/2/2025 02:30 | 18 | 19 | 2.75 | 7.281 | 4.121 | 7.07 | 57 | 1.93 | 68 | 0.343 | 0.018 | 45.89 | 10788 | 8.18 | 61 |  | 176.89 | 3.5 | 6.76 | -3.211 | 0.3
8/2/2025 02:45 | 19 | 19 | 2.75 | 6.675 | 5.787 | 7.06 | 57 | 1.93 | 68 | 0.343 | 0.018 | 45.89 | 10788 | 8.18 | 61 |  | 162.5 | 3.51 | 6.75 | -3.211 | 0.29
8/2/2025 03:00 | 17 | 19 | 2.75 | 6.682 | 5.323 | 7.07 | 57 | 1.93 | 68 | 0.343 | 0.018 | 45.89 | 10788 | 8.18 | 61 |  | 162.3 | 3.5 | 6.75 | -3.211 | 0.29
8/2/2025 03:15 | 21 | 19 | 2.75 | 6.833 | 5.123 | 7.07 | 57 | 1.93 | 68 | 0.343 | 0.018 | 45.89 | 10788 | 8.17 | 61 |  | 165.34 | 3.48 | 6.75 | -3.211 | 0.3
8/2/2025 03:30 | 18 | 19 | 2.75 | 6.915 | 4.885 | 7.08 | 57 | 1.93 | 68 | 0.343 | 0.018 | 45.89 | 10788 | 8.17 | 61 |  | 167.87 | 3.5 | 6.75 | -3.211 | 0.3
8/2/2025 03:45 | 18 | 19 | 2.75 | 6.916 | 4.441 | 7.09 | 57 | 1.93 | 68 | 0.343 | 0.018 | 45.89 | 10788 | 8.17 | 61 |  | 168.11 | 3.5 | 6.77 | -3.211 | 0.3
8/2/2025 04:00 | 15 | 19 | 2.75 | 6.912 | 4.214 | 7.11 | 57 | 1.93 | 68 | 0.42 | 0.018 | 45.89 | 10788 | 8.16 | 61 |  | 168.32 | 3.51 | 6.78 | -3.211 | 0.29
8/2/2025 04:15 | 13 | 19 | 2.75 | 6.926 | 4.148 | 7.11 | 57 | 1.93 | 68 | 0.42 | 0.018 | 45.89 | 10788 | 8.16 | 61 |  | 168.8 | 3.51 | 6.78 | -3.211 | 0.29
8/2/2025 04:30 | 16 | 19 | 2.75 | 7.411 | 3.638 | 7.11 | 57 | 1.93 | 68 | 0.42 | 0.018 | 45.89 | 10788 | 8.16 | 61 |  | 177.56 | 3.45 | 6.77 | -3.211 | 0.31
8/2/2025 04:45 | 17 | 19 | 2.75 | 7.425 | 4.051 | 7.09 | 57 | 1.93 | 68 | 0.42 | 0.019 | 45.82 | 10819 | 8.16 | 61 |  | 178.2 | 3.46 | 6.76 | -3.211 | 0.33
8/2/2025 05:00 | 18 | 19 | 2.75 | 7.395 | 3.827 | 7.07 | 57 | 1.93 | 68 | 0.42 | 0.019 | 45.82 | 10819 | 8.15 | 61 |  | 177.3 | 3.45 | 6.74 | -3.211 | 0.33
8/2/2025 05:15 | 21 | 19 | 2.75 | 7.031 | 3.874 | 7.08 | 57 | 1.93 | 68 | 0.42 | 0.02 | 45.82 | 10819 | 8.15 | 61 |  | 171.86 | 3.52 | 6.75 | -3.211 | 0.34
8/2/2025 05:30 | 18 | 19 | 2.75 | 7.146 | 3.66 | 7.08 | 57 | 1.93 | 68 | 0.42 | 0.02 | 45.82 | 10819 | 8.15 | 61 |  | 172.64 | 3.48 | 6.76 | -3.211 | 0.37
8/2/2025 05:45 | 23 | 19 | 2.75 | 7.576 | 3.513 | 7.09 | 57 | 1.93 | 68 | 0.42 | 0.019 | 45.82 | 10819 | 8.14 | 61 |  | 177.42 | 3.37 | 6.76 | -3.211 | 0.35
8/2/2025 06:00 | 24 | 19 | 2.75 | 7.53 | 3.457 | 7.1 | 57 | 1.93 | 67.8 | 0.42 | 0.019 | 45.82 | 10819 | 8.1 | 61 |  | 177.7 | 3.4 | 6.76 | -3.211 | 0.36
8/2/2025 06:15 | 27 | 19 | 2.75 | 6.877 | 3.771 | 7.09 | 57 | 1.93 | 67.8 | 0.42 | 0.02 | 45.82 | 10819 | 8.09 | 61 |  | 168.24 | 3.52 | 6.77 | -3.211 | 0.32
8/2/2025 06:30 | 22 | 19 | 2.75 | 6.891 | 3.877 | 7.09 | 57 | 1.93 | 67.8 | 0.42 | 0.019 | 45.82 | 10819 | 8.11 | 61 |  | 167.73 | 3.51 | 6.77 | -3.211 | 0.31
8/2/2025 06:45 | 22 | 19 | 2.75 | 7.623 | 3.678 | 7.1 | 57 | 1.93 | 67.8 | 0.42 | 0.019 | 45.82 | 10819 | 8.13 | 61 |  | 177.05 | 3.34 | 6.78 | -3.211 | 0.31
8/2/2025 07:00 | 20 | 19 | 2.75 | 7.626 | 3.95 | 7.11 | 57 | 1.93 | 67.8 | 0.42 | 0.019 | 45.82 | 10819 | 8.15 | 61 |  | 176.49 | 3.33 | 6.77 | -3.211 | 0.3
8/2/2025 07:15 | 17 | 19 | 2.75 | 7.618 | 3.796 | 7.12 | 57 | 1.93 | 67.8 | 0.42 | 0.019 | 45.82 | 10819 | 8.15 | 61 |  | 176.9 | 3.34 | 6.79 | -3.211 | 0.3
8/2/2025 07:30 | 15 | 19 | 2.75 | 7.629 | 3.809 | 7.12 | 57 | 1.93 | 67.8 | 0.42 | 0.019 | 45.82 | 10819 | 8.14 | 61 |  | 176.92 | 3.34 | 6.79 | -3.211 | 0.31
8/2/2025 07:45 | 16 | 19 | 2.75 | 7.046 | 4.019 | 7.12 | 57 | 1.93 | 67.8 | 0.42 | 0.019 | 45.82 | 10819 | 8.13 | 61 |  | 171.62 | 3.51 | 6.79 | -3.211 | 0.32
8/2/2025 08:00 | 16 | 19 | 2.75 | 7.111 | 3.711 | 7.13 | 57 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.12 | 61 |  | 172.81 | 3.5 | 6.8 | -3.211 | 0.33
8/2/2025 08:15 | 17 | 19 | 2.75 | 7.473 | 3.472 | 7.14 | 57 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.1 | 61 |  | 176.37 | 3.4 | 6.8 | -3.211 | 0.32
8/2/2025 08:30 | 20 | 19 | 2.75 | 7.476 | 3.454 | 7.14 | 57 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.1 | 61 |  | 176.61 | 3.4 | 6.8 | -3.211 | 0.33
8/2/2025 08:45 | 21 | 19 | 2.75 | 7.482 | 3.404 | 7.14 | 57 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.1 | 61 |  | 176.84 | 3.4 | 6.81 | -3.211 | 0.31
8/2/2025 09:00 | 21 | 19 | 2.75 | 7.454 | 3.33 | 7.14 | 57 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.09 | 61 |  | 176.08 | 3.4 | 6.81 | -3.211 | 0.3
8/2/2025 09:15 | 24 | 19 | 2.75 | 7.458 | 3.465 | 7.15 | 57 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.09 | 61 |  | 176.46 | 3.41 | 6.82 | -3.211 | 0.32
8/2/2025 09:30 | 23 | 19 | 2.75 | 7.461 | 3.493 | 7.14 | 57 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.09 | 61 |  | 176.35 | 3.4 | 6.81 | -3.211 | 0.34
8/2/2025 09:45 | 23 | 19 | 2.75 | 7.412 | 3.385 | 7.14 | 57 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.09 | 61 |  | 176.41 | 3.43 | 6.81 | -3.211 | 0.35
8/2/2025 10:00 | 25 | 19 | 2.75 | 7.46 | 3.307 | 7.14 | 58 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.09 | 61 |  | 180.16 | 3.48 | 6.81 | -3.211 | 0.33
8/2/2025 10:15 | 26 | 19 | 2.75 | 7.449 | 3.416 | 7.12 | 58 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.09 | 61 |  | 180.44 | 3.49 | 6.8 | -3.211 | 0.32
8/2/2025 10:30 | 27 | 19 | 2.75 | 7.43 | 3.521 | 7.12 | 58 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.1 | 61 |  | 180.5 | 3.5 | 6.8 | -3.211 | 0.34
8/2/2025 10:45 | 27 | 19 | 2.75 | 7.406 | 3.516 | 7.12 | 58 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.11 | 61 |  | 180.11 | 3.5 | 6.79 | -3.211 | 0.33
8/2/2025 11:00 | 27 | 19 | 2.75 | 6.791 | 3.686 | 7.11 | 58 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.13 | 61 |  | 165.06 | 3.5 | 6.8 | -3.211 | 0.34
8/2/2025 11:15 | 28 | 19 | 2.75 | 6.766 | 3.591 | 7.11 | 58 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.14 | 61 |  | 164.96 | 3.51 | 6.8 | -3.211 | 0.33
8/2/2025 11:30 | 26 | 19 | 2.75 | 7.346 | 3.285 | 7.11 | 58 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.15 | 61 |  | 178.25 | 3.49 | 6.79 | -3.211 | 0.32
8/2/2025 11:45 | 27 | 19 | 2.75 | 7.305 | 4.844 | 7.06 | 58 | 1.93 | 67.8 | 0.465 | 0.019 | 45.82 | 10819 | 8.16 | 61 |  | 177.79 | 3.5 | 6.73 | -3.211 | 0.29
8/2/2025 12:00 | 26 | 19 | 2.75 | 7.284 | 2.616 | 7.08 | 58 | 1.93 | 67.8 | 0.293 | 0.018 | 45.82 | 10819 | 8.16 | 61 |  | 177.79 | 3.51 | 6.71 | -3.211 | 0.29
8/2/2025 12:15 | 25 | 19 | 2.75 | 6.84 | 2.497 | 7.1 | 58 | 1.93 | 67.8 | 0.293 | 0.018 | 45.82 | 10819 | 8.16 | 61 |  | 165.59 | 3.49 | 6.71 | -3.211 | 0.29
8/2/2025 12:30 | 24 | 19 | 2.75 | 6.95 | 2.564 | 7.11 | 58 | 1.93 | 67.8 | 0.293 | 0.018 | 45.82 | 10819 | 8.17 | 61 |  | 170.77 | 3.54 | 6.78 | -3.211 | 0.29
8/2/2025 12:45 | 28 | 19 | 2.75 | 7.176 | 2.89 | 7.11 | 58 | 1.93 | 67.8 | 0.293 | 0.018 | 45.82 | 10819 | 8.17 | 61 |  | 174.65 | 3.5 | 6.78 | -3.211 | 0.28
8/2/2025 13:00 | 22 | 19 | 2.75 | 7.213 | 3.175 | 7.1 | 58 | 1.93 | 67.8 | 0.293 | 0.018 | 45.82 | 10819 | 8.17 | 61 |  | 174.86 | 3.49 | 6.8 | -3.211 | 0.28
8/2/2025 13:15 | 25 | 19 | 2.75 | 7.186 | 3.064 | 7.11 | 58 | 1.93 | 67.8 | 0.293 | 0.018 | 45.82 | 10819 | 8.16 | 61 |  | 175.91 | 3.53 | 6.8 | -3.211 | 0.28
8/2/2025 13:30 | 26 | 19 | 2.75 | 7.232 | 2.989 | 7.11 | 58 | 1.93 | 67.8 | 0.293 | 0.018 | 45.82 | 10819 | 8.16 | 61 |  | 175.07 | 3.49 | 6.8 | -3.211 | 0.28
8/2/2025 13:45 | 27 | 19 | 2.75 | 7.195 | 3.04 | 7.11 | 58 | 1.93 | 67.8 | 0.293 | 0.018 | 45.82 | 10819 | 8.16 | 61 |  | 175.21 | 3.51 | 6.8 | -3.211 | 0.3
8/2/2025 14:00 | 26 | 19 | 2.75 | 6.936 | 3.147 | 7.1 | 58 | 1.93 | 68 | 0.293 | 0.018 | 45.82 | 10819 | 8.16 | 60 |  | 168.7 | 3.5 | 6.8 | -3.211 | 0.29
8/2/2025 14:15 | 26 | 19 | 2.75 | 6.919 | 3.31 | 7.09 | 58 | 1.93 | 68 | 0.293 | 0.018 | 45.82 | 10819 | 8.15 | 60 |  | 168.72 | 3.51 | 6.78 | -3.211 | 0.29
8/2/2025 14:30 | 26 | 19 | 2.75 | 7.154 | 3.036 | 7.1 | 58 | 1.93 | 68 | 0.293 | 0.018 | 45.82 | 10819 | 8.14 | 60 |  | 74.85 | 1.51 | 6.79 | -3.211 | 0.29
8/2/2025 14:45 | 24 | 19 | 2.75 | 7.16 | 2.964 | 7.15 | 58 | 1.93 | 68 | 0.293 | 0.018 | 45.82 | 10819 | 8.14 | 60 |  | 74.91 | 1.51 | 6.83 | -3.211 | 0.3
8/2/2025 15:00 | 27 | 19 | 2.75 | 7.13 | 3.075 | 7.14 | 58 | 1.93 | 68 | 0.293 | 0.018 | 45.82 | 10819 | 8.13 | 60 |  | 74.7 | 1.51 | 6.85 | -3.211 | 0.31
8/2/2025 15:15 | 24 | 19 | 2.75 | 7.107 | 2.965 | 7.13 | 58 | 1.93 | 68 | 0.293 | 0.018 | 45.82 | 10819 | 8.12 | 60 |  | 74.9 | 1.52 | 6.82 | -3.211 | 0.31
8/2/2025 15:30 | 19 | 19 | 2.75 | 6.577 | 3.261 | 7.12 | 58 | 1.93 | 68 | 0.293 | 0.019 | 45.82 | 10819 | 8.11 | 60 |  | 68.95 | 1.51 | 6.8 | -3.211 | 0.31
8/2/2025 15:45 | 22 | 19 | 2.75 | 6.596 | 2.978 | 7.13 | 58 | 1.93 | 68 | 0.293 | 0.019 | 45.82 | 10819 | 8.12 | 60 |  | 68.82 | 1.5 | 6.81 | -3.211 | 0.31
8/2/2025 16:00 | 22 | 19 | 2.75 | 6.795 | 3.053 | 7.14 | 58 | 1.93 | 68 | 0.302 | 0.019 | 45.82 | 10819 | 8.14 | 60 |  | 70.45 | 1.49 | 6.81 | -3.211 | 0.32
8/2/2025 16:15 | 22 | 19 | 2.75 | 6.795 | 3.422 | 7.13 | 58 | 1.93 | 68 | 0.302 | 0.019 | 45.82 | 10819 | 8.15 | 60 |  | 70.77 | 1.5 | 6.79 | -3.211 | 0.29
8/2/2025 16:30 | 22 | 19 | 2.75 | 6.793 | 4.003 | 7.13 | 58 | 1.93 | 68 | 0.302 | 0.019 | 45.82 | 10819 | 8.17 | 60 |  | 70.53 | 1.5 | 6.78 | -3.211 | 0.28
8/2/2025 16:45 | 17 | 19 | 2.75 | 6.794 | 4.402 | 7.11 | 58 | 1.93 | 68 | 0.302 | 0.019 | 45.82 | 10819 | 8.19 | 60 |  | 70.74 | 1.5 | 6.77 | -3.211 | 0.28
8/2/2025 17:00 | 17 | 19 | 2.75 | 6.792 | 4.422 | 7.11 | 58 | 1.93 | 68 | 0.302 | 0.018 | 45.82 | 10819 | 8.2 | 60 |  | 70.48 | 1.49 | 6.77 | -3.211 | 0.3
8/2/2025 17:15 | 16 | 19 | 2.75 | 6.836 | 4.456 | 7.11 | 58 | 1.93 | 68 | 0.302 | 0.018 | 45.82 | 10819 | 8.21 | 60 |  | 70.95 | 1.49 | 6.77 | -3.211 | 0.28
8/2/2025 17:30 | 14 | 19 | 2.75 | 6.795 | 3.603 | 7.13 | 58 | 1.93 | 68 | 0.302 | 0.018 | 45.82 | 10819 | 8.23 | 60 |  | 71.09 | 1.51 | 6.8 | -3.211 | 0.3
8/2/2025 17:45 | 13 | 19 | 2.75 | 6.766 | 3.293 | 7.16 | 58 | 1.93 | 68 | 0.302 | 0.018 | 45.82 | 10819 | 8.23 | 60 |  | 70.77 | 1.51 | 6.83 | -3.211 | 0.3
8/2/2025 18:00 | 13 | 19 | 2.75 | 6.478 | 3.129 | 7.18 | 58 | 1.93 | 68 | 0.302 | 0.018 | 45.82 | 10819 | 8.23 | 60 |  | 68.02 | 1.51 | 6.86 | -3.211 | 0.28
8/2/2025 18:15 | 18 | 19 | 2.75 | 6.497 | 3.654 | 7.14 | 58 | 1.93 | 68 | 0.302 | 0.018 | 45.82 | 10819 | 8.23 | 60 |  | 68.03 | 1.51 | 6.81 | -3.211 | 0.28
8/2/2025 18:30 | 20 | 19 | 2.75 | 7.123 | 3.781 | 7.13 | 58 | 1.93 | 68 | 0.302 | 0.018 | 45.82 | 10819 | 8.23 | 60 |  | 73.52 | 1.49 | 6.81 | -3.211 | 0.29
8/2/2025 18:45 | 16 | 19 | 2.75 | 7.092 | 4.262 | 7.12 | 58 | 1.93 | 68 | 0.302 | 0.018 | 45.82 | 10819 | 8.23 | 60 |  | 73.53 | 1.49 | 6.78 | -3.211 | 0.27
8/2/2025 19:00 | 15 | 19 | 2.75 | 6.907 | 4.331 | 7.12 | 58 | 1.93 | 68 | 0.302 | 0.018 | 45.82 | 10819 | 8.23 | 60 |  | 72.69 | 1.52 | 6.77 | -3.211 | 0.28
8/2/2025 19:15 | 13 | 19 | 2.75 | 6.411 | 4.161 | 7.13 | 58 | 1.93 | 68 | 0.302 | 0.018 | 45.82 | 10819 | 8.23 | 60 |  | 67.51 | 1.52 | 6.78 | -3.211 | 0.27
8/2/2025 19:30 | 14 | 19 | 2.75 | 6.93 | 3.703 | 7.14 | 58 | 1.93 | 68 | 0.302 | 0.018 | 45.82 | 10819 | 8.23 | 60 |  | 71.07 | 1.48 | 6.8 | -3.211 | 0.29
8/2/2025 19:45 | 16 | 19 | 2.75 | 7.42 | 3.736 | 7.14 | 58 | 1.93 | 68 | 0.302 | 0.018 | 45.82 | 10819 | 8.23 | 60 |  | 76.79 | 1.49 | 6.79 | -3.211 | 0.3
8/2/2025 20:00 | 17 | 19 | 2.75 | 7.371 | 3.754 | 7.13 | 58 | 1.93 | 68 | 0.253 | 0.019 | 46.87 | 10977 | 8.23 | 60 |  | 77.45 | 1.51 | 6.77 | -3.211 | 0.29
8/2/2025 20:15 | 16 | 19 | 2.75 | 7.374 | 4.016 | 7.11 | 58 | 1.93 | 68 | 0.253 | 0.02 | 46.87 | 10977 | 8.22 | 60 |  | 77.18 | 1.51 | 6.75 | -3.211 | 0.3
8/2/2025 20:30 | 19 | 19 | 2.75 | 7.408 | 3.918 | 7.11 | 58 | 1.93 | 68 | 0.253 | 0.02 | 46.87 | 10977 | 8.21 | 60 |  | 77.26 | 1.5 | 6.75 | -3.211 | 0.3
8/2/2025 20:45 | 15 | 19 | 2.75 | 6.932 | 3.873 | 7.11 | 58 | 1.93 | 68 | 0.253 | 0.02 | 46.87 | 10977 | 8.22 | 60 |  | 71.88 | 1.49 | 6.78 | -3.211 | 0.29
8/2/2025 21:00 | 17 | 19 | 2.75 | 6.386 | 3.618 | 7.12 | 58 | 1.93 | 68 | 0.253 | 0.019 | 46.87 | 10977 | 8.23 | 60 |  | 67.16 | 1.51 | 6.8 | -3.211 | 0.32
8/2/2025 21:15 | 12 | 19 | 2.75 | 6.419 | 3.557 | 7.12 | 58 | 1.93 | 68 | 0.253 | 0.019 | 46.87 | 10977 | 8.21 | 60 |  | 66.89 | 1.5 | 6.82 | -3.211 | 0.3
8/2/2025 21:30 | 14 | 19 | 2.75 | 6.905 | 3.474 | 7.13 | 58 | 1.93 | 68 | 0.253 | 0.019 | 46.87 | 10977 | 8.2 | 60 |  | 71.94 | 1.5 | 6.81 | -3.211 | 0.29
8/2/2025 21:45 | 17 | 19 | 2.75 | 6.876 | 3.3 | 7.13 | 58 | 1.93 | 68 | 0.253 | 0.019 | 46.87 | 10977 | 8.23 | 60 |  | 71.88 | 1.51 | 6.8 | -3.211 | 0.3
8/2/2025 22:00 | 17 | 19 | 2.75 | 6.899 | 3.473 | 7.13 | 57 | 1.93 | 67.8 | 0.253 | 0.019 | 46.87 | 10977 | 8.25 | 60 |  | 72.22 | 1.51 | 6.8 | -3.211 | 0.28
8/2/2025 22:15 | 19 | 19 | 2.75 | 6.929 | 3.579 | 7.14 | 57 | 1.93 | 67.8 | 0.253 | 0.019 | 46.87 | 10977 | 8.28 | 60 |  | 144.46 | 3 | 6.82 | -3.211 | 0.28
8/2/2025 22:30 | 12 | 19 | 2.75 | 6.879 | 3.467 | 7.14 | 57 | 1.93 | 67.8 | 0.253 | 0.019 | 46.87 | 10977 | 8.29 | 60 |  | 144.03 | 3.02 | 6.82 | -3.211 | 0.28
8/2/2025 22:45 | 12 | 19 | 2.75 | 6.491 | 3.751 | 7.12 | 57 | 1.93 | 67.8 | 0.253 | 0.019 | 46.87 | 10977 | 8.29 | 60 |  | 135.69 | 3.01 | 6.81 | -3.211 | 0.27
8/2/2025 23:00 | 10 | 19 | 2.75 | 6.527 | 3.952 | 7.11 | 57 | 1.93 | 67.8 | 0.253 | 0.019 | 46.87 | 10977 | 8.29 | 60 |  | 136.48 | 3.01 | 6.81 | -3.211 | 0.28
8/2/2025 23:15 | 14 | 19 | 2.75 | 6.97 | 4.324 | 7.1 | 57 | 1.93 | 67.8 | 0.253 | 0.019 | 46.87 | 10977 | 8.29 | 60 |  | 145.28 | 3 | 6.79 | -3.211 | 0.27
8/2/2025 23:30 | 10 | 19 | 2.75 | 7.002 | 4.589 | 7.09 | 57 | 1.93 | 67.8 | 0.253 | 0.019 | 46.87 | 10977 | 8.28 | 60 |  | 145.54 | 2.99 | 6.78 | -3.211 | 0.27
8/2/2025 23:45 | 8 | 19 | 2.75 | 6.957 | 4.796 | 7.09 | 57 | 1.93 | 67.8 | 0.253 | 0.019 | 46.87 | 10977 | 8.29 | 60 |  | 145.38 | 3.01 | 6.8 | -3.211 | 0.29
8/3/2025 00:00 | 7 | 19 | 2.75 | 6.989 | 37.448 | 7.08 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.29 | 60 |  | 145.98 | 3.01 | 6.8 | -3.211 | 0.31
8/3/2025 00:15 | 6 | 19 | 2.75 | 6.955 | 9.822 | 7.08 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.3 | 60 |  | 144.87 | 3 | 6.8 | -3.211 | 0.3
8/3/2025 00:30 | 13 | 19 | 2.75 | 6.946 | 4.35 | 7.09 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.3 | 60 |  | 145.26 | 3.01 | 6.81 | -3.211 | 0.3
8/3/2025 00:45 | 13 | 19 | 2.75 | 6.914 | 3.612 | 7.1 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.31 | 60 |  | 145.39 | 3.03 | 6.83 | -3.211 | 0.29
8/3/2025 01:00 | 13 | 19 | 2.75 | 6.954 | 3.077 | 7.14 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.31 | 60 |  | 144.72 | 3 | 6.85 | -3.211 | 0.29
8/3/2025 01:15 | 19 | 19 | 2.75 | 6.933 | 2.848 | 7.16 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.31 | 60 |  | 144.48 | 3 | 6.87 | -3.211 | 0.29
8/3/2025 01:30 | 15 | 19 | 2.75 | 6.667 | 2.807 | 7.16 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.31 | 60 |  | 139.85 | 3.02 | 6.86 | -3.211 | 0.28
8/3/2025 01:45 | 12 | 19 | 2.75 | 6.56 | 2.646 | 7.14 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.31 | 60 |  | 136.93 | 3.01 | 6.85 | -3.211 | 0.28
8/3/2025 02:00 | 14 | 19 | 2.75 | 7.146 | 3.723 | 7.11 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.31 | 60 |  | 148.67 | 3 | 6.82 | -3.211 | 0.27
8/3/2025 02:15 | 15 | 19 | 2.75 | 7.251 | 3.695 | 7.09 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.31 | 60 |  | 150.58 | 2.99 | 6.8 | -3.211 | 0.28
8/3/2025 02:30 | 8 | 19 | 2.75 | 7.227 | 3.713 | 7.08 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.31 | 60 |  | 151.16 | 3.01 | 6.78 | -3.211 | 0.27
8/3/2025 02:45 | 11 | 19 | 2.75 | 6.596 | 3.396 | 7.09 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.31 | 60 |  | 138.27 | 3.02 | 6.78 | -3.211 | 0.28
8/3/2025 03:00 | 10 | 19 | 2.75 | 6.635 | 3.367 | 7.08 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.32 | 60 |  | 137.92 | 2.99 | 6.78 | -3.211 | 0.29
8/3/2025 03:15 | 10 | 19 | 2.75 | 6.651 | 3.394 | 7.08 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.32 | 60 |  | 139.23 | 3.01 | 6.78 | -3.211 | 0.29
8/3/2025 03:30 | 12 | 19 | 2.75 | 6.93 | 3.64 | 7.08 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.32 | 60 |  | 144.72 | 3.01 | 6.78 | -3.211 | 0.28
8/3/2025 03:45 | 11 | 19 | 2.75 | 6.98 | 3.487 | 7.08 | 57 | 1.93 | 67.8 | 0.326 | 0.019 | 46.87 | 10977 | 8.32 | 60 |  | 145.07 | 2.99 | 6.77 | -3.211 | 0.29
8/3/2025 04:00 | 11 | 19 | 2.75 | 6.91 | 3.327 | 7.08 | 57 | 1.93 | 67.8 | 0.416 | 0.019 | 46.87 | 10977 | 8.32 | 60 |  | 144.88 | 3.02 | 6.78 | -3.211 | 0.29
8/3/2025 04:15 | 8 | 19 | 2.75 | 6.499 | 3.295 | 7.1 | 57 | 1.93 | 67.8 | 0.416 | 0.019 | 46.87 | 10977 | 8.32 | 60 |  | 67.95 | 1.51 | 6.79 | -3.211 | 0.3
8/3/2025 04:30 | 10 | 19 | 2.75 | 6.726 | 3.261 | 7.1 | 57 | 1.93 | 67.8 | 0.416 | 0.019 | 46.87 | 10977 | 8.33 | 60 |  | 69.13 | 1.48 | 6.79 | -3.211 | 0.29
8/3/2025 04:45 | 13 | 19 | 2.75 | 6.94 | 3.375 | 7.11 | 57 | 1.93 | 67.8 | 0.416 | 0.019 | 46.87 | 10977 | 8.33 | 60 |  | 72.2 | 1.5 | 6.79 | -3.211 | 0.29
8/3/2025 05:00 | 15 | 19 | 2.75 | 6.965 | 3.158 | 7.12 | 57 | 1.93 | 67.8 | 0.416 | 0.019 | 46.87 | 10977 | 8.33 | 60 |  | 72.49 | 1.5 | 6.8 | -3.211 | 0.3
8/3/2025 05:15 | 11 | 19 | 2.75 | 6.731 | 3.054 | 7.13 | 57 | 1.93 | 67.8 | 0.416 | 0.019 | 46.87 | 10977 | 8.33 | 60 |  | 70.04 | 1.5 | 6.8 | -3.211 | 0.27
8/3/2025 05:30 | 13 | 19 | 2.75 | 6.56 | 3.524 | 7.12 | 57 | 1.93 | 67.8 | 0.416 | 0.019 | 46.87 | 10977 | 8.33 | 60 |  | 68.83 | 1.51 | 6.8 | -3.211 | 0.26
8/3/2025 05:45 | 14 | 19 | 2.75 | 6.931 | 3.734 | 7.11 | 57 | 1.93 | 67.8 | 0.416 | 0.019 | 46.87 | 10977 | 8.34 | 60 |  | 72.04 | 1.5 | 6.78 | -3.211 | 0.26
8/3/2025 06:00 | 13 | 19 | 2.75 | 6.88 | 4.549 | 7.09 | 57 | 1.93 | 67.6 | 0.416 | 0.019 | 46.87 | 10977 | 8.34 | 60 |  | 72.19 | 1.51 | 6.78 | -3.211 | 0.26
8/3/2025 06:15 | 1 | 19 | 2.75 | 6.884 | 4.581 | 7.08 | 57 | 1.93 | 67.6 | 0.416 | 0.024 | 46.87 | 10977 | 8.33 | 60 |  | 72.41 | 1.51 | 6.77 | -3.211 | 0.26
8/3/2025 06:30 | 4 | 19 | 2.75 | 6.887 | 4.432 | 7.1 | 57 | 1.93 | 67.6 | 0.416 | 0.019 | 46.87 | 10977 | 8.32 | 60 |  | 71.84 | 1.5 | 6.78 | -3.211 | 0.27
8/3/2025 06:45 | 2 | 19 | 2.75 | 6.885 | 4.325 | 7.11 | 57 | 1.93 | 67.6 | 0.416 | 0.018 | 46.87 | 10977 | 8.31 | 60 |  | 72.07 | 1.51 | 6.79 | -3.211 | 0.28
8/3/2025 07:00 | 9 | 19 | 2.75 | 6.858 | 4.06 | 7.12 | 57 | 1.93 | 67.6 | 0.416 | 0.018 | 46.87 | 10977 | 8.3 | 60 |  | 71.91 | 1.51 | 6.81 | -3.211 | 0.27
8/3/2025 07:15 | 5 | 19 | 2.75 | 6.88 | 3.894 | 7.13 | 57 | 1.93 | 67.6 | 0.416 | 0.019 | 46.87 | 10977 | 8.29 | 60 |  | 71.91 | 1.51 | 6.82 | -3.211 | 0.27
8/3/2025 07:30 | 10 | 19 | 2.75 | 7.062 | 3.945 | 7.13 | 57 | 1.93 | 67.6 | 0.416 | 0.019 | 47.75 | 10955 | 8.29 | 60 |  | 74 | 1.51 | 6.83 | -3.211 | 0.3
8/3/2025 07:45 | 13 | 19 | 2.75 | 7.092 | 3.699 | 7.14 | 57 | 1.93 | 67.6 | 0.416 | 0.019 | 47.75 | 10955 | 8.29 | 60 |  | 74.02 | 1.5 | 6.83 | -3.211 | 0.28
8/3/2025 08:00 | 14 | 19 | 2.75 | 7.038 | 3.703 | 7.14 | 57 | 1.93 | 67.6 | 0.387 | 0.02 | 47.75 | 10955 | 8.28 | 60 |  | 73.72 | 1.51 | 6.84 | -3.211 | 0.26
8/3/2025 08:15 | 13 | 19 | 2.75 | 7.079 | 4.003 | 7.14 | 57 | 1.93 | 67.6 | 0.387 | 0.02 | 47.75 | 10955 | 8.28 | 60 |  | 73.82 | 1.5 | 6.83 | -3.211 | 0.25
8/3/2025 08:30 | 12 | 19 | 2.75 | 7.099 | 4.18 | 7.14 | 57 | 1.93 | 67.6 | 0.387 | 0.02 | 47.75 | 10955 | 8.27 | 60 |  | 73.77 | 1.5 | 6.82 | -3.211 | 0.29
8/3/2025 08:45 | 12 | 19 | 2.75 | 7.063 | 4.277 | 7.09 | 57 | 1.93 | 67.6 | 0.387 | 0.019 | 47.75 | 10955 | 8.23 | 60 |  | 73.83 | 1.51 | 6.77 | -3.211 | 0.41
8/3/2025 09:00 | 9 | 19 | 2.75 | 7.044 | 3.915 | 7.11 | 57 | 1.93 | 67.6 | 0.387 | 0.019 | 47.75 | 10955 | 8.21 | 60 |  | 73.75 | 1.51 | 6.75 | -3.211 | 0.18
8/3/2025 09:15 | -23 | 19 | 2.75 | 7.086 | 4.014 | 7.12 | 57 | 1.93 | 67.6 | 0.387 | 0.019 | 47.75 | 10955 | 8.22 | 60 |  | 74.13 | 1.51 | 6.8 | -3.211 | 0.09
8/3/2025 09:30 | -20 | 19 | 2.75 | 7.058 | 4.018 | 7.12 | 57 | 1.93 | 67.6 | 0.387 | 0.019 | 47.75 | 10955 | 8.24 | 60 |  | 74.09 | 1.51 | 6.84 | -3.211 | 0
8/3/2025 09:45 | -21 | 19 | 2.75 | 7.056 | 4.08 | 7.12 | 57 | 1.93 | 67.6 | 0.387 | 0.019 | 47.75 | 10955 | 8.26 | 60 |  | 74.26 | 1.52 | 6.83 | -3.211 | 0.26
8/3/2025 10:00 | -39 | 19 | 2.75 | 7.083 | 4.003 | 7.13 | 60 | 1.93 | 67.6 | 0.387 | 0.019 | 47.75 | 10955 | 8.27 | 60 |  | 74.19 | 1.51 | 6.83 | -3.211 | 0.26
8/3/2025 10:15 | 1 | 19 | 2.75 | 7.038 | 3.894 | 7.13 | 60 | 1.93 | 67.6 | 0.387 | 0.019 | 47.75 | 10955 | 8.27 | 60 |  | 74.28 | 1.52 | 6.84 | -3.211 | 0.26
8/3/2025 10:30 | 7 | 19 | 2.75 | 7.031 | 3.804 | 7.13 | 60 | 1.93 | 67.6 | 0.387 | 0.019 | 47.75 | 10955 | 8.27 | 60 |  | 73.54 | 1.51 | 6.83 | -3.211 | 0.26
8/3/2025 10:45 | 9 | 19 | 2.75 | 7.06 | 3.918 | 7.12 | 60 | 1.93 | 67.6 | 0.387 | 0.019 | 47.75 | 10955 | 8.27 | 60 |  | 73.83 | 1.51 | 6.83 | -3.211 | 0.27
8/3/2025 11:00 | 9 | 19 | 2.75 | 6.88 | 3.749 | 7.14 | 60 | 1.93 | 67.6 | 0.387 | 0.019 | 47.75 | 10955 | 8.27 | 60 |  | 72.26 | 1.51 | 6.83 | -3.211 | 0.27
8/3/2025 11:15 | 5 | 19 | 2.75 | 6.624 | 3.744 | 7.14 | 60 | 1.93 | 67.6 | 0.387 | 0.019 | 47.75 | 10955 | 8.28 | 60 |  | 69.32 | 1.51 | 6.84 | -3.211 | 0.27
8/3/2025 11:30 | 1 | 19 | 2.75 | 6.88 | 3.699 | 7.14 | 60 | 1.93 | 67.6 | 0.387 | 0.019 | 47.75 | 10955 | 8.28 | 60 |  | 71.4 | 1.49 | 6.83 | -3.211 | 0.28
8/3/2025 11:45 | 6 | 19 | 2.75 | 6.889 | 3.743 | 7.14 | 60 | 1.93 | 67.6 | 0.387 | 0.019 | 47.75 | 10955 | 8.27 | 60 |  | 72.03 | 1.51 | 6.83 | -3.211 | 0.3
8/3/2025 12:00 | 11 | 19 | 2.75 | 6.872 | 3.526 | 7.14 | 60 | 1.93 | 67.6 | 0.212 | 0.019 | 47.75 | 10955 | 8.28 | 60 |  | 72.2 | 1.51 | 6.83 | -3.211 | 0.26
8/3/2025 12:15 | 9 | 19 | 2.75 | 6.861 | 3.287 | 7.17 | 60 | 1.93 | 67.6 | 0.212 | 0.019 | 47.75 | 10955 | 8.28 | 60 |  | 71.72 | 1.51 | 6.85 | -3.211 | 0.28
8/3/2025 12:30 | 12 | 19 | 2.75 | 6.903 | 3.186 | 7.18 | 60 | 1.93 | 67.6 | 0.212 | 0.019 | 47.75 | 10955 | 8.28 | 60 |  | 72.14 | 1.5 | 6.86 | -3.211 | 0.29
8/3/2025 12:45 | 5 | 19 | 2.75 | 6.822 | 3.102 | 7.17 | 60 | 1.93 | 67.6 | 0.212 | 0.019 | 47.75 | 10955 | 8.28 | 60 |  | 71.9 | 1.52 | 6.86 | -3.211 | 0.29
8/3/2025 13:00 | 6 | 19 | 2.75 | 6.894 | 2.991 | 7.17 | 60 | 1.93 | 67.6 | 0.212 | 0.019 | 47.75 | 10955 | 8.28 | 60 |  | 71.8 | 1.5 | 6.85 | -3.211 | 0.29
8/3/2025 13:15 | 8 | 19 | 2.75 | 6.847 | 3.114 | 7.17 | 60 | 1.93 | 67.6 | 0.212 | 0.019 | 47.75 | 10955 | 8.28 | 60 |  | 72.07 | 1.52 | 6.84 | -3.211 | 0.32
8/3/2025 13:30 | 12 | 19 | 2.75 | 6.845 | 3.261 | 7.16 | 60 | 1.93 | 67.6 | 0.212 | 0.019 | 47.75 | 10955 | 8.29 | 60 |  | 71.55 | 1.51 | 6.83 | -3.211 | 0.29
8/3/2025 13:45 | 12 | 19 | 2.75 | 6.846 | 3.321 | 7.16 | 60 | 1.93 | 67.6 | 0.212 | 0.019 | 47.75 | 10955 | 8.29 | 60 |  | 72.18 | 1.52 | 6.83 | -3.211 | 0.3
8/3/2025 14:00 | 13 | 19 | 2.75 | 6.906 | 3.457 | 7.16 | 60 | 1.93 | 68 | 0.212 | 0.019 | 47.75 | 10955 | 8.29 | 59 |  | 71.81 | 1.5 | 6.83 | -3.211 | 0.28
8/3/2025 14:15 | 12 | 19 | 2.75 | 6.866 | 3.409 | 7.15 | 60 | 1.93 | 68 | 0.212 | 0.019 | 47.75 | 10955 | 8.29 | 59 |  | 71.83 | 1.51 | 6.83 | -3.211 | 0.29
8/3/2025 14:30 | 10 | 19 | 2.75 | 6.836 | 3.567 | 7.15 | 60 | 1.93 | 68 | 0.212 | 0.019 | 47.75 | 10955 | 8.29 | 59 |  | 71.36 | 1.5 | 6.83 | -3.211 | 0.28
8/3/2025 14:45 | 14 | 19 | 2.75 | 6.834 | 3.485 | 7.14 | 60 | 1.93 | 68 | 0.212 | 0.019 | 47.75 | 10955 | 8.29 | 59 |  | 71.63 | 1.51 | 6.83 | -3.211 | 0.29
8/3/2025 15:00 | 16 | 19 | 2.75 | 6.799 | 3.356 | 7.15 | 60 | 1.93 | 68 | 0.212 | 0.019 | 47.75 | 10955 | 8.29 | 59 |  | 71.28 | 1.51 | 6.83 | -3.211 | 0.3
8/3/2025 15:15 | 16 | 19 | 2.75 | 6.419 | 3.26 | 7.16 | 60 | 1.93 | 68 | 0.212 | 0.019 | 47.75 | 10955 | 8.29 | 59 |  | 67.45 | 1.51 | 6.84 | -3.211 | 0.29
8/3/2025 15:30 | 18 | 19 | 2.75 | 6.776 | 3.316 | 7.15 | 60 | 1.93 | 68 | 0.212 | 0.019 | 47.75 | 10955 | 8.28 | 59 |  | 70.14 | 1.49 | 6.84 | -3.211 | 0.29
8/3/2025 15:45 | 17 | 19 | 2.75 | 6.736 | 3.494 | 7.14 | 60 | 1.93 | 68 | 0.212 | 0.019 | 47.75 | 10955 | 8.28 | 59 |  | 70.27 | 1.5 | 6.83 | -3.211 | 0.3
8/3/2025 16:00 | 16 | 19 | 2.75 | 6.746 | 3.549 | 7.14 | 60 | 1.93 | 68 | 0.212 | 0.019 | 47.75 | 10955 | 8.28 | 59 |  | 70.68 | 1.51 | 6.82 | -3.211 | 0.29
8/3/2025 16:15 | 18 | 19 | 2.75 | 6.738 | 3.617 | 7.14 | 60 | 1.93 | 68 | 0.212 | 0.019 | 47.75 | 10955 | 8.28 | 59 |  | 70.58 | 1.51 | 6.82 | -3.211 | 0.29
8/3/2025 16:30 | 18 | 19 | 2.75 | 7.299 | 3.542 | 7.14 | 60 | 1.93 | 68 | 0.212 | 0.019 | 47.75 | 10955 | 8.28 | 59 |  | 75.79 | 1.5 | 6.82 | -3.211 | 0.29
8/3/2025 16:45 | 17 | 19 | 2.75 | 7.265 | 3.477 | 7.15 | 60 | 1.93 | 68 | 0.212 | 0.019 | 47.75 | 10955 | 8.28 | 59 |  | 75.52 | 1.5 | 6.83 | -3.211 | 0.29
8/3/2025 17:00 | 16 | 19 | 2.75 | 7.292 | 3.506 | 7.15 | 60 | 1.93 | 68 | 0.212 | 0.02 | 47.75 | 10955 | 8.28 | 59 |  | 75.34 | 1.49 | 6.84 | -3.211 | 0.29
8/3/2025 17:15 | 18 | 19 | 2.75 | 7.23 | 3.349 | 7.16 | 60 | 1.93 | 68 | 0.212 | 0.02 | 47.75 | 10955 | 8.28 | 59 |  | 75.44 | 1.5 | 6.84 | -3.211 | 0.3
8/3/2025 17:30 | 19 | 19 | 2.75 | 6.612 | 3.361 | 7.16 | 60 | 1.93 | 68 | 0.212 | 0.02 | 47.75 | 10955 | 8.28 | 59 |  | 69.39 | 1.51 | 6.84 | -3.211 | 0.29
8/3/2025 17:45 | 20 | 19 | 2.75 | 6.631 | 3.505 | 7.16 | 60 | 1.93 | 68 | 0.212 | 0.02 | 47.75 | 10955 | 8.28 | 59 |  | 69.22 | 1.5 | 6.85 | -3.211 | 0.29
8/3/2025 18:00 | 22 | 19 | 2.75 | 7.193 | 3.786 | 7.16 | 60 | 1.93 | 68 | 0.212 | 0.02 | 47.75 | 10955 | 8.28 | 59 |  | 74.85 | 1.5 | 6.85 | -3.211 | 0.32
8/3/2025 18:15 | 14 | 19 | 2.75 | 7.195 | 5.191 | 7.14 | 60 | 1.93 | 68 | 0.212 | 0.02 | 49.11 | 11017 | 8.28 | 59 |  | 75.13 | 1.5 | 6.83 | -3.211 | 0.3
8/3/2025 18:30 | 16 | 19 | 2.75 | 7.19 | 39.936 | 7.15 | 60 | 1.93 | 68 | 0.212 | 0.021 | 49.11 | 11017 | 8.29 | 59 |  | 75.16 | 1.51 | 6.83 | -3.211 | 0.3
8/3/2025 18:45 | 14 | 19 | 2.75 | 7.748 | 13.816 | 7.16 | 60 | 1.93 | 68 | 0.212 | 0.021 | 49.11 | 11017 | 8.3 | 59 |  | 80.03 | 1.49 | 6.84 | -3.211 | 0.3
8/3/2025 19:00 | 15 | 19 | 2.75 | 7.689 | 6.441 | 7.15 | 60 | 1.93 | 68 | 0.212 | 0.021 | 49.11 | 11017 | 8.3 | 59 |  | 80.49 | 1.51 | 6.82 | -3.211 | 0.29
8/3/2025 19:15 | 17 | 19 | 2.75 | 7.703 | 5.381 | 7.14 | 60 | 1.93 | 68 | 0.212 | 0.021 | 49.11 | 11017 | 8.28 | 59 |  | 80.28 | 1.5 | 6.82 | -3.211 | 0.3
8/3/2025 19:30 | 18 | 19 | 2.75 | 7.405 | 4.482 | 7.14 | 60 | 1.93 | 68 | 0.212 | 0.022 | 49.11 | 11017 | 8.25 | 59 |  | 77.99 | 1.52 | 6.82 | -3.211 | 0.31
8/3/2025 19:45 | 17 | 19 | 2.75 | 7.415 | 3.772 | 7.14 | 60 | 1.93 | 68 | 0.212 | 0.021 | 49.11 | 11017 | 8.25 | 59 |  | 77.67 | 1.51 | 6.83 | -3.211 | 0.3
8/3/2025 20:00 | 18 | 19 | 2.75 | 7.451 | 3.706 | 7.14 | 60 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.27 | 59 |  | 77.43 | 1.5 | 6.83 | -3.211 | 0.29
8/3/2025 20:15 | 18 | 19 | 2.75 | 7.408 | 3.242 | 7.14 | 60 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.29 | 59 |  | 77.38 | 1.5 | 6.83 | -3.211 | 0.29
8/3/2025 20:30 | 16 | 19 | 2.75 | 7.433 | 3.075 | 7.14 | 60 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.3 | 59 |  | 77.67 | 1.5 | 6.83 | -3.211 | 0.29
8/3/2025 20:45 | 16 | 19 | 2.75 | 7.408 | 3.077 | 7.14 | 60 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.31 | 59 |  | 77.4 | 1.5 | 6.83 | -3.211 | 0.29
8/3/2025 21:00 | 21 | 19 | 2.75 | 7.081 | 3.214 | 7.14 | 60 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.31 | 59 |  | 74.34 | 1.51 | 6.82 | -3.211 | 0.29
8/3/2025 21:15 | 18 | 19 | 2.75 | 6.852 | 3.035 | 7.13 | 60 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.3 | 59 |  | 141.86 | 2.98 | 6.83 | -3.211 | 0.3
8/3/2025 21:30 | 18 | 19 | 2.75 | 7.138 | 3.261 | 7.11 | 60 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.3 | 59 |  | 148.87 | 3 | 6.83 | -3.211 | 0.29
8/3/2025 21:45 | 19 | 19 | 2.75 | 7.113 | 2.987 | 7.1 | 60 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.29 | 59 |  | 149 | 3.02 | 6.83 | -3.211 | 0.28
8/3/2025 22:00 | 17 | 19 | 2.75 | 7.168 | 3.087 | 7.1 | 58 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.28 | 59 |  | 149.18 | 3 | 6.82 | -3.211 | 0.28
8/3/2025 22:15 | 19 | 19 | 2.75 | 7.138 | 3.067 | 7.1 | 58 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.27 | 59 |  | 148.63 | 3 | 6.81 | -3.211 | 0.29
8/3/2025 22:30 | 18 | 19 | 2.75 | 7.151 | 3.171 | 7.09 | 58 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.27 | 59 |  | 149.06 | 3 | 6.8 | -3.211 | 0.28
8/3/2025 22:45 | 14 | 19 | 2.75 | 7.116 | 3.044 | 7.09 | 58 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.27 | 59 |  | 148.4 | 3 | 6.8 | -3.211 | 0.29
8/3/2025 23:00 | 13 | 19 | 2.75 | 7.111 | 3.031 | 7.09 | 58 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.27 | 59 |  | 148.48 | 3.01 | 6.78 | -3.211 | 0.29
8/3/2025 23:15 | 15 | 19 | 2.75 | 7.369 | 4.288 | 7.09 | 58 | 1.93 | 68 | 0.246 | 0.021 | 49.11 | 11017 | 8.27 | 59 |  | 153.83 | 3.01 | 6.79 | -3.211 | 0.32
8/3/2025 23:30 | 13 | 19 | 2.75 | 7.368 | 3.478 | 7.1 | 58 | 1.93 | 68 | 0.246 | 0.021 | 49.77 | 11142 | 8.27 | 59 |  | 153.93 | 3.01 | 6.79 | -3.211 | 0.29
8/3/2025 23:45 | 14 | 19 | 2.75 | 7.596 | 3.345 | 7.1 | 58 | 1.93 | 68 | 0.246 | 0.021 | 49.77 | 11142 | 8.27 | 59 |  | 158.52 | 3.01 | 6.79 | -3.211 | 0.29
8/4/2025 00:00 | 15 | 19 | 2.75 | 7.599 | 3.215 | 7.1 | 58 | 1.93 | 68 | 0.318 | 0.022 | 49.77 | 11142 | 8.27 | 59 |  | 158.34 | 3 | 6.79 | -3.211 | 0.3
8/4/2025 00:15 | 12 | 19 | 2.75 | 7.613 | 3.031 | 7.11 | 58 | 1.93 | 68 | 0.318 | 0.022 | 49.77 | 11142 | 8.27 | 59 |  | 158.07 | 2.99 | 6.8 | -3.211 | 0.3
8/4/2025 00:30 | 14 | 19 | 2.75 | 7.329 | 3.032 | 7.11 | 58 | 1.93 | 68 | 0.318 | 0.022 | 49.77 | 11142 | 8.26 | 59 |  | 153.68 | 3.02 | 6.82 | -3.211 | 0.3
8/4/2025 00:45 | 18 | 19 | 2.75 | 7.254 | 3.126 | 7.1 | 58 | 1.93 | 68 | 0.318 | 0.021 | 49.77 | 11142 | 8.23 | 59 |  | 150.59 | 2.99 | 6.82 | -3.211 | 0.28
8/4/2025 01:00 | 19 | 19 | 2.75 | 7.589 | 3.25 | 7.1 | 58 | 1.93 | 68 | 0.318 | 0.021 | 49.77 | 11142 | 8.22 | 59 |  | 157.15 | 2.98 | 6.83 | -3.211 | 0.29
8/4/2025 01:15 | 14 | 19 | 2.75 | 7.53 | 3.323 | 7.09 | 58 | 1.93 | 68 | 0.318 | 0.021 | 49.77 | 11142 | 8.23 | 59 |  | 157.63 | 3.01 | 6.83 | -3.211 | 0.29
8/4/2025 01:30 | 15 | 19 | 2.75 | 7.556 | 3.209 | 7.09 | 58 | 1.93 | 68 | 0.318 | 0.021 | 49.77 | 11142 | 8.26 | 59 |  | 157.51 | 3 | 6.82 | -3.211 | 0.29
8/4/2025 01:45 | 15 | 19 | 2.75 | 7.548 | 3.217 | 7.09 | 58 | 1.93 | 68 | 0.318 | 0.021 | 49.77 | 11142 | 8.27 | 59 |  | 157.4 | 3 | 6.83 | -3.211 | 0.3
8/4/2025 02:00 | 14 | 19 | 2.75 | 7.511 | 3.108 | 7.09 | 58 | 1.93 | 68 | 0.318 | 0.021 | 49.77 | 11142 | 8.27 | 59 |  | 157.2 | 3.01 | 6.82 | -3.211 | 0.29
8/4/2025 02:15 | 15 | 19 | 2.75 | 7.527 | 3.029 | 7.09 | 58 | 1.93 | 68 | 0.318 | 0.021 | 49.77 | 11142 | 8.27 | 59 |  | 157.09 | 3.01 | 6.83 | -3.211 | 0.28
8/4/2025 02:30 | 17 | 19 | 2.75 | 7.547 | 3.292 | 7.09 | 58 | 1.93 | 68 | 0.318 | 0.021 | 49.77 | 11142 | 8.27 | 59 |  | 157.72 | 3.01 | 6.82 | -3.211 | 0.29
8/4/2025 02:45 | 19 | 19 | 2.75 | 7.516 | 3.332 | 7.08 | 58 | 1.93 | 68 | 0.318 | 0.021 | 49.77 | 11142 | 8.26 | 59 |  | 156.8 | 3 | 6.82 | -3.211 | 0.28
8/4/2025 03:00 | 16 | 19 | 2.75 | 7.552 | 3.276 | 7.08 | 58 | 1.93 | 68 | 0.318 | 0.021 | 49.77 | 11142 | 8.26 | 59 |  | 157.34 | 3 | 6.81 | -3.211 | 0.3
8/4/2025 03:15 | 15 | 19 | 2.75 | 7.584 | 3.349 | 7.08 | 58 | 1.93 | 68 | 0.318 | 0.021 | 49.77 | 11142 | 8.26 | 59 |  | 157.33 | 2.99 | 6.81 | -3.211 | 0.29
8/4/2025 03:30 | 16 | 19 | 2.75 | 7.857 | 3.482 | 7.08 | 58 | 1.93 | 68 | 0.318 | 0.021 | 50.71 | 11237 | 8.26 | 59 |  | 164.11 | 3.01 | 6.8 | -3.211 | 0.27
8/4/2025 03:45 | 13 | 19 | 2.75 | 7.852 | 3.561 | 7.07 | 58 | 1.93 | 68 | 0.318 | 0.022 | 50.71 | 11237 | 8.26 | 59 |  | 135.6 | 2.49 | 6.79 | -3.211 | 0.27
8/4/2025 04:00 | 13 | 19 | 2.75 | 7.861 | 39.937 | 7.06 | 58 | 1.93 | 68 | 0.417 | 0.022 | 50.71 | 11237 | 8.26 | 59 |  | 164.46 | 3.01 | 6.78 | -3.211 | 0.26
8/4/2025 04:15 | 8 | 19 | 2.75 | 7.882 | 5.495 | 7.06 | 58 | 1.93 | 68 | 0.417 | 0.022 | 50.71 | 11237 | 8.26 | 59 |  | 163.28 | 2.98 | 6.78 | -3.211 | 0.28
8/4/2025 04:30 | 11 | 19 | 2.75 | 7.84 | 4.097 | 7.06 | 58 | 1.93 | 68 | 0.417 | 0.022 | 50.71 | 11237 | 8.25 | 59 |  | 163.25 | 3 | 6.79 | -3.211 | 0.3
8/4/2025 04:45 | 10 | 19 | 2.75 | 7.844 | 3.925 | 7.06 | 58 | 1.93 | 68 | 0.417 | 0.022 | 50.71 | 11237 | 8.23 | 59 |  | 163.9 | 3.01 | 6.79 | -3.211 | 0.27
8/4/2025 05:00 | 14 | 19 | 2.75 | 7.858 | 3.784 | 7.06 | 58 | 1.93 | 68 | 0.417 | 0.022 | 50.71 | 11237 | 8.23 | 59 |  | 164.48 | 3.01 | 6.8 | -3.211 | 0.28
8/4/2025 05:15 | 11 | 19 | 2.75 | 8.116 | 3.537 | 7.06 | 58 | 1.93 | 68 | 0.417 | 0.021 | 50.71 | 11237 | 8.27 | 59 |  | 169.65 | 3.01 | 6.8 | -3.211 | 0.28
8/4/2025 05:30 | 10 | 19 | 2.75 | 8.127 | 3.557 | 7.06 | 58 | 1.93 | 68 | 0.417 | 0.021 | 50.71 | 11237 | 8.3 | 59 |  | 169.49 | 3 | 6.79 | -3.211 | 0.28
8/4/2025 05:45 | 11 | 19 | 2.75 | 8.097 | 3.611 | 7.05 | 58 | 1.93 | 68 | 0.417 | 0.021 | 50.71 | 11237 | 8.3 | 59 |  | 169.39 | 3.01 | 6.79 | -3.211 | 0.29
8/4/2025 06:00 | 12 | 19 | 2.75 | 7.476 | 3.82 | 7.05 | 58 | 1.93 | 67.8 | 0.417 | 0.021 | 50.71 | 11237 | 8.3 | 59 |  | 157.4 | 3.03 | 6.79 | -3.211 | 0.29
8/4/2025 06:15 | 10 | 19 | 2.75 | 7.506 | 3.81 | 7.04 | 58 | 1.93 | 67.8 | 0.417 | 0.021 | 50.71 | 11237 | 8.29 | 59 |  | 155.68 | 2.99 | 6.79 | -3.211 | 0.27
8/4/2025 06:30 | 11 | 19 | 2.75 | 7.649 | 3.603 | 7.04 | 58 | 1.93 | 67.8 | 0.417 | 0.021 | 50.71 | 11237 | 8.28 | 59 |  | 158.8 | 2.99 | 6.8 | -3.211 | 0.29
8/4/2025 06:45 | 5 | 19 | 2.75 | 7.633 | 3.72 | 7.04 | 58 | 1.93 | 67.8 | 0.417 | 0.021 | 50.71 | 11237 | 8.27 | 59 |  | 159.76 | 3.01 | 6.8 | -3.211 | 0.28
8/4/2025 07:00 | 9 | 19 | 2.75 | 7.653 | 3.528 | 7.05 | 58 | 1.93 | 67.8 | 0.417 | 0.021 | 50.71 | 11237 | 8.26 | 59 |  | 159.21 | 3 | 6.8 | -3.211 | 0.27
8/4/2025 07:15 | 12 | 19 | 2.75 | 7.895 | 3.61 | 7.05 | 58 | 1.93 | 67.8 | 0.417 | 0.021 | 50.71 | 11237 | 8.26 | 59 |  | 164.84 | 3.01 | 6.79 | -3.211 | 0.28
8/4/2025 07:30 | 10 | 19 | 2.75 | 7.897 | 3.528 | 7.05 | 58 | 1.93 | 67.8 | 0.417 | 0.021 | 50.71 | 11237 | 8.25 | 59 |  | 164.59 | 3 | 6.79 | -3.211 | 0.27
8/4/2025 07:45 | 11 | 19 | 2.75 | 7.866 | 3.609 | 7.05 | 58 | 1.93 | 67.8 | 0.417 | 0.021 | 50.71 | 11237 | 8.25 | 59 |  | 164.29 | 3.01 | 6.8 | -3.211 | 0.3
8/4/2025 08:00 | 8 | 19 | 2.75 | 7.437 | 3.668 | 7.06 | 58 | 1.93 | 67.8 | 0.465 | 0.021 | 50.71 | 11237 | 8.24 | 59 |  | 154.39 | 2.99 | 6.81 | -3.211 | 0.28
8/4/2025 08:15 | 11 | 19 | 2.75 | 7.464 | 3.543 | 7.06 | 58 | 1.93 | 67.8 | 0.465 | 0.021 | 50.71 | 11237 | 8.24 | 59 |  | 154.91 | 2.99 | 6.82 | -3.211 | 1.15
8/4/2025 08:30 | 3 | 19 | 2.75 | 7.679 | 3.057 | 7.04 | 58 | 1.93 | 67.8 | 0.465 | 0.021 | 50.71 | 11237 | 8.24 | 59 |  | 160.58 | 3.01 | 6.8 | -3.211 | 0.29
8/4/2025 08:45 | -11 | 19 | 2.75 | 7.673 | 2.848 | 7.06 | 58 | 1.93 | 67.8 | 0.465 | 0.023 | 50.71 | 11237 | 8.23 | 59 |  | 160.03 | 3 | 6.74 | -3.211 | 0.29
8/4/2025 09:00 | 1 | 19 | 2.75 | 7.679 | 2.868 | 7.07 | 58 | 1.93 | 67.8 | 0.465 | 0.02 | 50.71 | 11237 | 8.23 | 59 |  | 160.01 | 3 | 6.75 | -3.211 | 0.3
8/4/2025 09:15 | 3 | 19 | 2.75 | 7.7 | 2.797 | 7.08 | 58 | 1.93 | 67.8 | 0.465 | 0.02 | 50.71 | 11237 | 8.22 | 59 |  | 160.64 | 3 | 6.82 | -3.211 | 0.3
8/4/2025 09:30 | 6 | 19 | 2.75 | 7.694 | 2.708 | 7.08 | 58 | 1.93 | 67.8 | 0.465 | 0.02 | 50.71 | 11237 | 8.22 | 59 |  | 160.27 | 3 | 6.83 | -3.211 | 0.29
8/4/2025 09:45 | 8 | 19 | 2.75 | 7.658 | 2.623 | 7.08 | 58 | 1.93 | 67.8 | 0.465 | 0.02 | 50.71 | 11237 | 8.22 | 59 |  | 160.2 | 3.01 | 6.83 | -3.211 | 0.31
8/4/2025 10:00 | 8 | 19 | 2.75 | 7.666 | 2.635 | 7.08 | 57 | 1.93 | 67.8 | 0.465 | 0.02 | 50.71 | 11237 | 8.22 | 59 |  | 160.35 | 3.01 | 6.82 | -3.211 | 0.3
8/4/2025 10:15 | 13 | 19 | 2.75 | 7.69 | 2.647 | 7.08 | 57 | 1.93 | 67.8 | 0.465 | 0.02 | 50.71 | 11237 | 8.22 | 59 |  | 160.13 | 3 | 6.82 | -3.211 | 0.31
8/4/2025 10:30 | 12 | 19 | 2.75 | 7.643 | 2.749 | 7.07 | 57 | 1.93 | 67.8 | 0.465 | 0.02 | 50.71 | 11237 | 8.21 | 59 |  | 159.87 | 3.01 | 6.81 | -3.211 | 0.31
8/4/2025 10:45 | 12 | 19 | 2.75 | 7.496 | 2.679 | 7.08 | 57 | 1.93 | 67.8 | 0.465 | 0.02 | 50.71 | 11237 | 8.21 | 59 |  | 156.5 | 3.01 | 6.82 | -3.211 | 0.31
8/4/2025 11:00 | 8 | 19 | 2.75 | 7.349 | 2.706 | 7.08 | 57 | 1.93 | 67.8 | 0.465 | 0.02 | 50.71 | 11237 | 8.2 | 59 |  | 113.8 | 2.23 | 6.82 | -3.211 | 0.31
8/4/2025 11:15 | 35 | 19 | 2.75 | 7.462 | 9.171 | 7.09 | 57 | 1.93 | 67.8 | 0.465 | 0.02 | 50.71 | 11237 | 8.21 | 59 |  | 155.91 | 3.01 | 6.82 | -3.211 | 0.3
8/4/2025 11:30 | 12 | 19 | 2.75 | 7.687 | 2.805 | 7.1 | 57 | 1.93 | 67.8 | 0.465 | 0.02 | 50.71 | 11237 | 8.21 | 59 |  | 160 | 3 | 6.82 | -3.211 | 0.28
8/4/2025 11:45 | 12 | 19 | 2.75 | 7.658 | 2.701 | 7.1 | 57 | 1.93 | 67.8 | 0.465 | 0.02 | 50.71 | 11237 | 8.2 | 59 |  | 160.05 | 3.01 | 6.82 | -3.211 | 0.3
8/4/2025 12:00 | 10 | 19 | 2.75 | 7.674 | 2.607 | 7.1 | 57 | 1.93 | 67.8 | 0.272 | 0.02 | 50.71 | 11237 | 8.19 | 59 |  | 159.89 | 3 | 6.82 | -5.019 | 0.29
8/4/2025 12:15 | 15 | 19 | 2.75 | 7.705 | 2.413 | 7.11 | 57 | 1.93 | 67.8 | 0.272 | 0.02 | 50.71 | 11237 | 8.2 | 59 |  | 159.62 | 2.98 | 6.83 | -5.019 | 0.29
8/4/2025 12:30 | 14 | 19 | 2.75 | 7.648 | 2.338 | 7.12 | 57 | 1.93 | 67.8 | 0.272 | 0.02 | 50.71 | 11237 | 8.2 | 59 |  | 160.18 | 3.02 | 6.83 | -5.019 | 0.3
8/4/2025 12:45 | 14 | 19 | 2.75 | 7.65 | 2.647 | 7.11 | 57 | 1.93 | 67.8 | 0.272 | 0.02 | 50.71 | 11237 | 8.21 | 59 |  | 160.04 | 3.01 | 6.82 | -5.019 | 0.29
8/4/2025 13:00 | 10 | 19 | 2.75 | 7.655 | 2.617 | 7.11 | 57 | 1.93 | 67.8 | 0.272 | 0.02 | 50.71 | 11237 | 8.2 | 59 |  | 159.6 | 3 | 6.82 | -5.019 | 0.29
8/4/2025 13:15 | 11 | 19 | 2.75 | 7.189 | 2.65 | 7.11 | 57 | 1.93 | 67.8 | 0.272 | 0.02 | 50.71 | 11237 | 8.2 | 59 |  | 149.6 | 3 | 6.82 | -5.019 | 0.29
8/4/2025 13:30 | 8 | 19 | 2.75 | 7.578 | 2.652 | 7.11 | 57 | 1.93 | 67.8 | 0.272 | 0.02 | 50.71 | 11237 | 8.2 | 59 |  | 157.85 | 3 | 6.83 | -5.019 | 0.29
8/4/2025 13:45 | 4 | 19 | 2.75 | 7.563 | 2.474 | 7.12 | 57 | 1.93 | 67.8 | 0.272 | 0.02 | 50.71 | 11237 | 8.19 | 59 |  | 157.49 | 3 | 6.83 | -5.019 | 0.27
8/4/2025 14:00 | 8 | 19 | 2.75 | 7.59 | 2.484 | 7.12 | 57 | 1.93 | 68 | 0.272 | 0.02 | 50.71 | 11237 | 8.19 | 59 |  | 158.18 | 3 | 6.83 | -5.019 | 0.28
8/4/2025 14:15 | 12 | 19 | 2.75 | 7.603 | 2.49 | 7.12 | 57 | 1.93 | 68 | 0.272 | 0.02 | 50.71 | 11237 | 8.18 | 59 |  | 157.84 | 2.99 | 6.84 | -5.019 | 0.28
8/4/2025 14:30 | 13 | 19 | 2.75 | 7.577 | 2.586 | 7.11 | 57 | 1.93 | 68 | 0.272 | 0.02 | 50.71 | 11237 | 8.17 | 59 |  | 158.03 | 3 | 6.83 | -5.019 | 0.29
8/4/2025 14:45 | 7 | 19 | 2.75 | 7.598 | 2.811 | 7.1 | 57 | 1.93 | 68 | 0.272 | 0.02 | 50.71 | 11237 | 8.16 | 59 |  | 157.68 | 2.99 | 6.81 | -5.019 | 0.29
8/4/2025 15:00 | 5 | 19 | 2.75 | 7.582 | 2.775 | 7.1 | 57 | 1.93 | 68 | 0.272 | 0.02 | 50.71 | 11237 | 8.16 | 59 |  | 158.27 | 3.01 | 6.81 | -5.019 | 0.29
8/4/2025 15:15 | 5 | 19 | 2.75 | 7.58 | 2.874 | 7.1 | 57 | 1.93 | 68 | 0.272 | 0.02 | 50.71 | 11237 | 8.16 | 59 |  | 157.45 | 2.99 | 6.82 | -5.019 | 0.28
8/4/2025 15:30 | 8 | 19 | 2.75 | 7.589 | 2.88 | 7.1 | 57 | 1.93 | 68 | 0.272 | 0.02 | 50.71 | 11237 | 8.15 | 59 |  | 158.24 | 3 | 6.82 | -5.019 | 0.29
8/4/2025 15:45 | 10 | 19 | 2.75 | 7.56 | 2.8 | 7.09 | 57 | 1.93 | 68 | 0.272 | 0.02 | 50.71 | 11237 | 8.15 | 59 |  | 157.58 | 3 | 6.82 | -5.019 | 0.28
8/4/2025 16:00 | 7 | 19 | 2.75 | 7.85 | 2.798 | 7.09 | 57 | 1.93 | 68 | 0.278 | 0.02 | 50.71 | 11237 | 8.15 | 59 |  | 162.97 | 2.99 | 6.82 | -5.019 | 0.28
8/4/2025 16:15 | 5 | 19 | 2.75 | 7.768 | 2.739 | 7.1 | 57 | 1.93 | 68 | 0.278 | 0.02 | 50.71 | 11237 | 8.15 | 59 |  | 163.22 | 3.03 | 6.82 | -5.019 | 0.31
8/4/2025 16:30 | 12 | 19 | 2.75 | 7.787 | 2.584 | 7.11 | 57 | 1.93 | 68 | 0.278 | 0.02 | 50.71 | 11237 | 8.15 | 59 |  | 162.82 | 3.01 | 6.83 | -5.019 | 0.28
8/4/2025 16:45 | 10 | 19 | 2.75 | 7.837 | 2.603 | 7.11 | 57 | 1.93 | 68 | 0.278 | 0.02 | 50.71 | 11237 | 8.15 | 59 |  | 162.83 | 2.99 | 6.83 | -5.019 | 0.28
8/4/2025 17:00 | 13 | 19 | 2.75 | 7.762 | 2.578 | 7.11 | 57 | 1.93 | 68 | 0.278 | 0.02 | 50.71 | 11237 | 8.15 | 59 |  | 162.18 | 3.01 | 6.83 | -5.019 | 0.28
8/4/2025 17:15 | 14 | 19 | 2.75 | 7.284 | 2.361 | 7.11 | 57 | 1.93 | 68 | 0.278 | 0.02 | 50.71 | 11237 | 8.15 | 59 |  | 151.83 | 3 | 6.84 | -5.019 | 0.3
8/4/2025 17:30 | 13 | 19 | 2.75 | 7.309 | 2.63 | 7.11 | 57 | 1.93 | 68 | 0.278 | 0.02 | 50.71 | 11237 | 8.15 | 59 |  | 151.98 | 2.99 | 6.85 | -5.019 | 0.29
8/4/2025 17:45 | 15 | 19 | 2.75 | 7.657 | 2.613 | 7.1 | 57 | 1.93 | 68 | 0.278 | 0.02 | 50.71 | 11237 | 8.16 | 59 |  | 159.66 | 3 | 6.83 | -5.019 | 0.29
8/4/2025 18:00 | 8 | 19 | 2.75 | 7.659 | 2.58 | 7.11 | 57 | 1.93 | 68.1 | 0.278 | 0.02 | 50.71 | 11237 | 8.17 | 59 |  | 159.66 | 3 | 6.83 | -5.019 | 0.29
8/4/2025 18:15 | 12 | 19 | 2.75 | 7.621 | 2.444 | 7.11 | 57 | 1.93 | 68.1 | 0.278 | 0.02 | 50.71 | 11237 | 8.18 | 59 |  | 158.98 | 3 | 6.84 | -5.019 | 0.27
8/4/2025 18:30 | 15 | 19 | 2.75 | 7.653 | 2.358 | 7.12 | 57 | 1.93 | 68.1 | 0.278 | 0.02 | 50.71 | 11237 | 8.18 | 59 |  | 159.28 | 3 | 6.85 | -5.019 | 0.27
8/4/2025 18:45 | 7 | 19 | 2.75 | 7.654 | 2.46 | 7.12 | 57 | 1.93 | 68.1 | 0.278 | 0.02 | 50.71 | 11237 | 8.18 | 59 |  | 159.58 | 3 | 6.84 | -5.019 | 0.27
8/4/2025 19:00 | 9 | 19 | 2.75 | 7.669 | 2.786 | 7.1 | 57 | 1.93 | 68.1 | 0.278 | 0.021 | 50.71 | 11237 | 8.19 | 59 |  | 159.39 | 2.99 | 6.82 | -5.019 | 0.27
8/4/2025 19:15 | 16 | 19 | 2.75 | 7.143 | 2.793 | 7.1 | 57 | 1.93 | 68.1 | 0.278 | 0.022 | 50.71 | 11237 | 8.19 | 59 |  | 149.46 | 3.01 | 6.81 | -5.019 | 0.28
8/4/2025 19:30 | 12 | 19 | 2.75 | 7.324 | 2.704 | 7.12 | 57 | 1.93 | 68.1 | 0.278 | 0.021 | 51.31 | 11236 | 8.19 | 59 |  | 153.34 | 3.01 | 6.82 | -5.019 | 0.27
8/4/2025 19:45 | 10 | 19 | 2.75 | 7.544 | 2.545 | 7.12 | 57 | 1.93 | 68.1 | 0.278 | 0.021 | 51.31 | 11236 | 8.19 | 59 |  | 157.54 | 3.01 | 6.83 | -5.019 | 0.29
8/4/2025 20:00 | 7 | 19 | 2.75 | 7.565 | 2.357 | 7.13 | 57 | 1.93 | 68.1 | 0.32 | 0.022 | 51.31 | 11236 | 8.19 | 59 |  | 157.59 | 3 | 6.83 | -5.019 | 0.28
8/4/2025 20:15 | 13 | 19 | 2.75 | 7.555 | 2.223 | 7.14 | 57 | 1.93 | 68.1 | 0.32 | 0.021 | 51.31 | 11236 | 8.19 | 59 |  | 158.2 | 3.02 | 6.85 | -5.019 | 0.27
8/4/2025 20:30 | 14 | 19 | 2.75 | 7.554 | 2.388 | 7.13 | 57 | 1.93 | 68.1 | 0.32 | 0.021 | 51.31 | 11236 | 8.18 | 59 |  | 157.62 | 3 | 6.84 | -5.019 | 0.27
8/4/2025 20:45 | 14 | 19 | 2.75 | 7.464 | 2.414 | 7.13 | 57 | 1.93 | 68.1 | 0.32 | 0.021 | 51.31 | 11236 | 8.16 | 59 |  | 155.16 | 2.99 | 6.87 | -5.019 | 0.27
8/4/2025 21:00 | 13 | 19 | 2.75 | 7.18 | 2.435 | 7.13 | 57 | 1.93 | 68.1 | 0.32 | 0.021 | 51.31 | 11236 | 8.15 | 59 |  | 149.95 | 3.01 | 6.82 | -5.019 | 0.28
8/4/2025 21:15 | 7 | 19 | 2.75 | 7.528 | 2.479 | 7.12 | 57 | 1.93 | 68.1 | 0.32 | 0.021 | 51.31 | 11236 | 8.17 | 59 |  | 157.25 | 3.01 | 6.81 | -5.019 | 0.28
8/4/2025 21:30 | 9 | 19 | 2.75 | 7.554 | 2.58 | 7.14 | 57 | 1.93 | 68.1 | 0.32 | 0.021 | 51.31 | 11236 | 8.19 | 59 |  | 0 | 0 | 6.83 | -5.019 | 0.29
8/4/2025 21:45 | 7 | 19 | 2.75 | 7.541 | 2.548 | 7.16 | 57 | 1.93 | 68.1 | 0.32 | 0.021 | 51.31 | 11236 | 8.2 | 59 |  | 0 | 0 | 6.86 | -5.019 | 0.28
8/4/2025 22:00 | 5 | 19 | 2.75 | 7.55 | 2.44 | 7.18 | 54 | 1.93 | 68.3 | 0.32 | 0.021 | 51.31 | 11236 | 8.21 | 59 |  | 0 | 0 | 6.89 | -5.019 | 0.28
8/4/2025 22:15 | 7 | 19 | 2.75 | 7.806 | 2.563 | 7.18 | 54 | 1.93 | 68.3 | 0.32 | 0.021 | 51.31 | 11236 | 8.21 | 59 |  | 0 | 0 | 6.89 | -5.019 | 0.28
8/4/2025 22:30 | 9 | 19 | 2.75 | 7.804 | 2.418 | 7.21 | 54 | 1.93 | 68.3 | 0.32 | 0.021 | 51.31 | 11236 | 8.2 | 59 |  | 0 | 0 | 6.89 | -5.019 | 0.27
8/4/2025 22:45 | 10 | 19 | 2.75 | 7.807 | 2.733 | 7.22 | 54 | 1.93 | 68.3 | 0.32 | 0.021 | 51.31 | 11236 | 8.19 | 59 |  | 0 | 0 | 6.88 | -5.019 | 0.26
8/4/2025 23:00 | 7 | 19 | 2.75 | 7.776 | 2.731 | 7.22 | 54 | 1.93 | 68.3 | 0.32 | 0.021 | 51.31 | 11236 | 8.19 | 59 |  | 0 | 0 | 6.88 | -5.019 | 0.27
8/4/2025 23:15 | 0 | 19 | 2.75 | 7.783 | 3.07 | 7.19 | 54 | 1.93 | 68.3 | 0.32 | 0.021 | 51.31 | 11236 | 8.19 | 59 |  | 0 | 0 | 6.86 | -5.019 | 0.26
8/4/2025 23:30 | 0 | 19 | 2.75 | 7.177 | 3.068 | 7.18 | 54 | 1.93 | 68.3 | 0.32 | 0.021 | 51.31 | 11236 | 8.19 | 59 |  | 74.18 | 1.49 | 6.85 | -5.019 | 0.27
8/4/2025 23:45 | -2 | 19 | 2.75 | 7.19 | 3.432 | 7.14 | 54 | 1.93 | 68.3 | 0.32 | 0.021 | 51.31 | 11236 | 8.2 | 59 |  | 74.52 | 1.49 | 6.84 | -5.019 | 0.26
8/5/2025 00:00 | -2 | 19 | 2.75 | 7.549 | 39.937 | 7.1 | 54 | 1.93 | 68.3 | 0.479 | 0.021 | 51.31 | 11236 | 8.2 | 59 |  | 156.87 | 2.99 | 6.82 | -5.019 | 0.27
8/5/2025 00:15 | 0 | 19 | 2.75 | 7.554 | 13.882 | 7.11 | 54 | 1.93 | 68.3 | 0.479 | 0.021 | 51.31 | 11236 | 8.21 | 59 |  | 156.87 | 2.99 | 6.82 | -5.019 | 0.24
8/5/2025 00:30 | -10 | 19 | 2.75 | 7.56 | 6.459 | 7.12 | 54 | 1.93 | 68.3 | 0.479 | 0.021 | 51.31 | 11236 | 8.21 | 59 |  | 157.83 | 3.01 | 6.82 | -5.019 | 0.27
8/5/2025 00:45 | -9 | 19 | 2.75 | 7.681 | 4.416 | 7.12 | 54 | 1.93 | 68.3 | 0.479 | 0.02 | 51.31 | 11236 | 8.22 | 59 |  | 160.17 | 3 | 6.82 | -5.019 | 0.25
8/5/2025 01:00 | 0 | 19 | 2.75 | 7.719 | 3.63 | 7.13 | 54 | 1.93 | 68.3 | 0.479 | 0.02 | 51.31 | 11236 | 8.22 | 59 |  | 160.03 | 2.99 | 6.82 | -5.019 | 0.32
8/5/2025 01:15 | -9 | 19 | 2.75 | 7.683 | 3.043 | 7.13 | 54 | 1.93 | 68.3 | 0.479 | 0.021 | 51.31 | 11236 | 8.23 | 59 |  | 160.11 | 3 | 6.84 | -5.019 | 0.26
8/5/2025 01:30 | 0 | 19 | 2.75 | 7.705 | 2.912 | 7.13 | 54 | 1.93 | 68.3 | 0.479 | 0.02 | 51.31 | 11236 | 8.24 | 59 |  | 159.55 | 2.98 | 6.83 | -5.019 | 0.25
8/5/2025 01:45 | 6 | 19 | 2.75 | 7.678 | 2.704 | 7.13 | 54 | 1.93 | 68.3 | 0.479 | 0.02 | 51.31 | 11236 | 8.25 | 59 |  | 159.93 | 3 | 6.83 | -5.019 | 0.26
8/5/2025 02:00 | 2 | 19 | 2.75 | 7.668 | 2.702 | 7.12 | 54 | 1.93 | 68.3 | 0.479 | 0.02 | 51.31 | 11236 | 8.25 | 60 |  | 160.12 | 3.01 | 6.83 | -5.019 | 0.27
8/5/2025 02:15 | 7 | 19 | 2.75 | 7.679 | 2.718 | 7.12 | 54 | 1.93 | 68.3 | 0.479 | 0.02 | 51.31 | 11236 | 8.26 | 60 |  | 160.23 | 3 | 6.83 | -5.019 | 0.25
8/5/2025 02:30 | 6 | 19 | 2.75 | 7.708 | 2.745 | 7.12 | 54 | 1.93 | 68.3 | 0.479 | 0.02 | 51.31 | 11236 | 8.27 | 60 |  | 160.33 | 3 | 6.83 | -5.019 | 0.26
8/5/2025 02:45 | 6 | 19 | 2.75 | 7.671 | 2.641 | 7.12 | 54 | 1.93 | 68.3 | 0.479 | 0.02 | 51.31 | 11236 | 8.28 | 60 |  | 160.44 | 3.01 | 6.83 | -5.019 | 0.26
8/5/2025 03:00 | 8 | 19 | 2.75 | 7.663 | 2.735 | 7.11 | 54 | 1.93 | 68.3 | 0.479 | 0.02 | 51.31 | 11236 | 8.28 | 60 |  | 159.9 | 3 | 6.83 | -5.019 | 0.24
8/5/2025 03:15 | 6 | 19 | 2.75 | 7.119 | 2.876 | 7.11 | 54 | 1.93 | 68.3 | 0.479 | 0.02 | 51.31 | 11236 | 8.28 | 60 |  | 148.02 | 2.99 | 6.82 | -5.019 | 0.22
8/5/2025 03:30 | 5 | 19 | 2.75 | 6.891 | 3.016 | 7.1 | 54 | 1.93 | 68.3 | 0.479 | 0.02 | 51.31 | 11236 | 8.28 | 60 |  | 143.03 | 2.99 | 6.82 | -5.019 | 0.21
8/5/2025 03:45 | 1 | 19 | 2.75 | 7.265 | 3.206 | 7.09 | 54 | 1.93 | 68.3 | 0.479 | 0.02 | 51.31 | 11236 | 8.28 | 60 |  | 151.44 | 3 | 6.8 | -5.019 | 0.22
8/5/2025 04:00 | -5 | 19 | 2.75 | 7.54 | 3.175 | 7.09 | 54 | 1.93 | 68.3 | 0.411 | 0.02 | 51.31 | 11236 | 8.28 | 60 |  | 157.07 | 3 | 6.8 | -5.019 | 0.24
8/5/2025 04:15 | -2 | 19 | 2.75 | 7.557 | 2.986 | 7.09 | 54 | 1.93 | 68.3 | 0.411 | 0.02 | 51.31 | 11236 | 8.28 | 60 |  | 157.32 | 3 | 6.8 | -5.019 | 0.23
8/5/2025 04:30 | -4 | 19 | 2.75 | 7.569 | 2.871 | 7.1 | 54 | 1.93 | 68.3 | 0.411 | 0.02 | 51.31 | 11236 | 8.29 | 60 |  | 157.38 | 2.99 | 6.81 | -5.019 | 0.12
8/5/2025 04:45 | 0 | 19 | 2.75 | 7.554 | 2.914 | 7.1 | 54 | 1.93 | 68.3 | 0.411 | 0.02 | 51.31 | 11236 | 8.29 | 60 |  | 157.02 | 2.99 | 6.8 | -5.019 | 0.2
8/5/2025 05:00 | 1 | 19 | 2.75 | 7.531 | 2.88 | 7.09 | 54 | 1.93 | 68.3 | 0.411 | 0.02 | 51.31 | 11236 | 8.28 | 60 |  | 157.37 | 3.01 | 6.8 | -5.019 | 0.25
8/5/2025 05:15 | 0 | 19 | 2.75 | 7.555 | 3.046 | 7.09 | 54 | 1.93 | 68.3 | 0.411 | 0.021 | 51.3 | 11247 | 8.27 | 60 |  | 156.82 | 2.99 | 6.79 | -5.019 | 0.26
8/5/2025 05:30 | 1 | 19 | 2.75 | 7.934 | 2.981 | 7.09 | 54 | 1.93 | 68.3 | 0.411 | 0.021 | 51.3 | 11247 | 8.27 | 60 |  | 164.99 | 2.99 | 6.79 | -5.019 | 0.28
8/5/2025 05:45 | -13 | 19 | 2.75 | 7.898 | 2.98 | 7.09 | 54 | 1.93 | 68.3 | 0.411 | 0.021 | 51.3 | 11247 | 8.26 | 60 |  | 164.68 | 3 | 6.8 | -5.019 | 0.25
8/5/2025 06:00 | 0 | 19 | 2.75 | 7.879 | 2.891 | 7.09 | 54 | 1.93 | 68.1 | 0.411 | 0.021 | 51.3 | 11247 | 8.24 | 60 |  | 164.42 | 3.01 | 6.8 | -5.019 | 0.27
8/5/2025 06:15 | 4 | 19 | 2.75 | 7.812 | 2.89 | 7.1 | 54 | 1.93 | 68.1 | 0.411 | 0.021 | 51.3 | 11247 | 8.21 | 60 |  | 163.22 | 3.01 | 6.82 | -5.019 | 0.26
8/5/2025 06:30 | 5 | 19 | 2.75 | 8.071 | 2.598 | 7.1 | 54 | 1.93 | 68.1 | 0.411 | 0.021 | 51.3 | 11247 | 8.21 | 60 |  | 168.8 | 3.01 | 6.83 | -5.019 | 0.26
8/5/2025 06:45 | 7 | 19 | 2.75 | 8.113 | 2.71 | 7.1 | 54 | 1.93 | 68.1 | 0.411 | 0.021 | 51.3 | 11247 | 8.23 | 60 |  | 168.32 | 2.99 | 6.83 | -5.019 | 0.25
8/5/2025 07:00 | 7 | 19 | 2.75 | 8.04 | 2.786 | 7.09 | 54 | 1.93 | 68.1 | 0.411 | 0.021 | 51.3 | 11247 | 8.25 | 60 |  | 167.74 | 3 | 6.82 | -5.019 | 0.21
8/5/2025 07:15 | 4 | 17 | 2.75 | 7.529 | 2.874 | 7.09 | 54 | 1.93 | 68.1 | 0.411 | 0.021 | 51.3 | 11247 | 8.26 | 60 |  | 157.69 | 3.02 | 6.86 | -5.019 | 0.17
8/5/2025 07:30 |  | 17 | 2.75 | 8.15 | 2.812 | 7.09 | 54 | 1.93 | 68.1 | 0.411 | 0.021 | 51.3 | 11247 | 8.26 | 60 |  | 169.1 | 2.99 | 6.85 | -5.019 | 0.19
8/5/2025 07:45 | -10 | 17 | 2.75 | 8.069 | 2.728 | 7.1 | 54 | 1.93 | 68.1 | 0.411 | 0.021 | 51.3 | 11247 | 8.25 | 60 |  | 168.56 | 3.01 | 6.99 | -5.019 | 0.18 | 96
8/5/2025 08:00 | -19 | 17 | 2.75 | 8.1 | 2.786 | 7.09 | 54 | 1.93 | 68.1 | 0.35 | 0.021 | 51.3 | 11247 | 8.24 | 60 |  | 168.14 | 2.99 | 6.82 | -5.019 | 0.3 | 91
8/5/2025 08:15 | 4 | 17 | 2.75 | 8.057 | 39.936 | 7.07 | 54 | 1.93 | 68.1 | 0.35 | 0.021 | 51.3 | 11247 | 8.23 | 60 |  | 168.24 | 3.01 | 6.79 | -5.019 | 0.26 | 101
8/5/2025 08:30 | 8 | 17 | 2.75 | 7.667 | 2.621 | 7.07 | 54 | 1.93 | 68.1 | 0.35 | 0.021 | 51.3 | 11247 | 8.22 | 60 |  | 160.27 | 3.01 | 6.83 | -5.019 | 0.28 | 101
8/5/2025 08:45 | 8 | 17 | 2.75 | 7.678 | 2.578 | 7.09 | 54 | 1.93 | 68.1 | 0.35 | 0.021 | 51.3 | 11247 | 8.21 | 60 |  | 159.59 | 2.99 | 6.87 | -5.019 | 0.3 | 101
8/5/2025 09:00 | 8 | 17 | 2.75 | 8.08 | 2.564 | 7.1 | 54 | 1.93 | 68.1 | 0.35 | 0.021 | 51.3 | 11247 | 8.21 | 60 |  | 168.62 | 3.01 | 6.88 | -5.019 | 0.31 | 101
8/5/2025 09:15 | 7 | 17 | 2.75 | 8.089 | 2.658 | 7.1 | 54 | 1.93 | 68.1 | 0.35 | 0.021 | 51.3 | 11247 | 8.2 | 60 |  | 168.71 | 3 | 6.87 | -5.019 | 0.29 | 101
8/5/2025 09:30 | 7 | 17 | 2.75 | 7.352 | 2.634 | 7.11 | 54 | 1.93 | 68.1 | 0.35 | 0.021 | 51.3 | 11247 | 8.2 | 60 |  | 153.72 | 3.01 | 6.86 | -5.019 | 0.3 | 101
8/5/2025 09:45 | 11 | 17 | 2.75 | 7.382 | 2.471 | 7.11 | 54 | 1.93 | 68.1 | 0.35 | 0.021 | 51.3 | 11247 | 8.19 | 60 |  | 153.61 | 3 | 6.86 | -5.019 | 0.31 | 101
8/5/2025 10:00 | 8 | 17 | 2.75 | 7.741 | 2.546 | 7.1 | 56 | 1.93 | 68.1 | 0.35 | 0.021 | 51.3 | 11247 | 8.19 | 60 |  | 160.76 | 2.99 | 6.85 | -5.019 | 0.31 | 101
8/5/2025 10:15 | 3 | 17 | 2.75 | 7.752 | 2.523 | 7.11 | 56 | 1.93 | 68.1 | 0.35 | 0.02 | 51.3 | 11247 | 8.2 | 60 |  | 161.52 | 3 | 6.85 | -5.019 | 0.31 | 101
8/5/2025 10:30 | 3 | 17 | 2.75 | 7.745 | 2.557 | 7.11 | 56 | 1.93 | 68.1 | 0.35 | 0.02 | 51.3 | 11247 | 8.2 | 60 |  | 161.12 | 3 | 6.85 | -5.019 | 0.3 | 101
8/5/2025 10:45 | 7 | 17 | 2.75 | 7.716 | 2.569 | 7.11 | 56 | 1.93 | 68.1 | 0.35 | 0.02 | 51.3 | 11247 | 8.2 | 60 |  | 161.06 | 3.01 | 6.84 | -5.019 | 0.32 | 101
8/5/2025 11:00 | 7 | 17 | 2.75 | 7.73 | 2.577 | 7.11 | 56 | 1.93 | 68.1 | 0.35 | 0.02 | 51.3 | 11247 | 8.21 | 60 |  | 160.9 | 3 | 6.84 | -5.019 | 0.31 | 101
8/5/2025 11:15 | 2 | 17 | 2.75 | 7.684 | 2.532 | 7.12 | 56 | 1.93 | 68.1 | 0.35 | 0.02 | 51.3 | 11247 | 8.21 | 60 |  | 160.6 | 3.01 | 6.85 | -5.019 | 0.32 | 101
8/5/2025 11:30 | 10 | 17 | 2.75 | 7.724 | 2.566 | 7.12 | 56 | 1.93 | 68.1 | 0.35 | 0.02 | 51.3 | 11247 | 8.22 | 60 |  | 160.86 | 3 | 6.85 | -5.019 | 0.31 | 101
8/5/2025 11:45 | 7 | 17 | 2.75 | 7.713 | 2.592 | 7.12 | 56 | 1.93 | 68.1 | 0.35 | 0.02 | 51.3 | 11247 | 8.22 | 60 |  | 161.38 | 3.01 | 6.85 | -5.019 | 0.3 | 101
8/5/2025 12:00 | 10 | 17 | 2.75 | 7.706 | 2.501 | 7.11 | 56 | 1.93 | 68.1 | 0.24 | 0.02 | 51.3 | 11247 | 8.22 | 60 |  | 180.53 | 3.37 | 6.84 | -5.019 | 0.31 | 101
8/5/2025 12:15 | 5 | 17 | 2.75 | 7.383 | 2.534 | 7.12 | 56 | 1.93 | 68.1 | 0.24 | 0.021 | 51.3 | 11247 | 8.22 | 60 |  | 179 | 3.49 | 6.85 | -5.019 | 0.3 | 101
8/5/2025 12:30 | 7 | 17 | 2.75 | 7.69 | 2.483 | 7.12 | 56 | 1.93 | 68.1 | 0.24 | 0.02 | 51.3 | 11247 | 8.22 | 60 |  | 180.41 | 3.38 | 6.85 | -5.019 | 0.31 | 101
8/5/2025 12:45 | 7 | 17 | 2.75 | 7.705 | 2.571 | 7.12 | 56 | 1.93 | 68.1 | 0.24 | 0.02 | 51.3 | 11247 | 8.22 | 60 |  | 180.24 | 3.37 | 6.84 | -5.019 | 0.3 | 101
8/5/2025 13:00 | 5 | 17 | 2.75 | 7.717 | 2.613 | 7.11 | 56 | 1.93 | 68.1 | 0.24 | 0.02 | 51.3 | 11247 | 8.22 | 60 |  | 180.75 | 3.37 | 6.84 | -5.019 | 0.29 | 101
8/5/2025 13:15 | 2 | 17 | 2.75 | 7.695 | 2.49 | 7.12 | 56 | 1.93 | 68.1 | 0.24 | 0.02 | 51.3 | 11247 | 8.22 | 60 |  | 180.76 | 3.38 | 6.84 | -5.019 | 0.31 | 101
8/5/2025 13:30 | 5 | 17 | 2.75 | 7.738 | 2.454 | 7.13 | 56 | 1.93 | 68.1 | 0.24 | 0.02 | 51.3 | 11247 | 8.22 | 60 |  | 180.44 | 3.36 | 6.85 | -5.019 | 0.31 | 101
8/5/2025 13:45 | 7 | 17 | 2.75 | 7.706 | 2.435 | 7.13 | 56 | 1.93 | 68.1 | 0.24 | 0.02 | 51.3 | 11247 | 8.22 | 60 |  | 180.53 | 3.37 | 6.86 | -5.019 | 0.3 | 101
8/5/2025 14:00 | 8 | 17 | 2.75 | 7.689 | 2.52 | 7.13 | 56 | 1.93 | 68.6 | 0.24 | 0.02 | 51.3 | 11247 | 8.21 | 57 |  | 181.07 | 3.39 | 6.86 | -5.019 | 0.28 | 101
8/5/2025 14:15 | 4 | 17 | 2.75 | 7.705 | 2.715 | 7.11 | 56 | 1.93 | 68.6 | 0.24 | 0.02 | 51.3 | 11247 | 8.21 | 57 |  | 181.15 | 3.39 | 6.85 | -5.019 | 0.28 | 101
8/5/2025 14:30 | 2 | 17 | 2.75 | 7.69 | 2.906 | 7.1 | 56 | 1.93 | 68.6 | 0.24 | 0.02 | 51.3 | 11247 | 8.21 | 57 |  | 181.14 | 3.39 | 6.84 | -5.019 | 0.28 | 101
8/5/2025 14:45 | 6 | 17 | 2.75 | 7.214 | 2.899 | 7.1 | 56 | 1.93 | 68.6 | 0.24 | 0.021 | 51.3 | 11247 | 8.21 | 57 |  | 175.96 | 3.51 | 6.85 | -5.019 | 0.29 | 101
8/5/2025 15:00 | 4 | 17 | 2.75 | 7.267 | 2.83 | 7.1 | 56 | 1.93 | 68.6 | 0.24 | 0.021 | 51.3 | 11247 | 8.21 | 57 |  | 176.62 | 3.5 | 6.84 | -5.019 | 0.28 | 101
8/5/2025 15:15 | 7 | 17 | 2.75 | 7.216 | 2.776 | 7.1 | 56 | 1.93 | 68.6 | 0.24 | 0.021 | 50.92 | 11182 | 8.21 | 57 |  | 176.36 | 3.52 | 6.84 | -5.019 | 0.29 | 101
8/5/2025 15:30 | 9 | 17 | 2.75 | 6.703 | 2.7 | 7.11 | 56 | 1.93 | 68.6 | 0.24 | 0.022 | 50.92 | 11182 | 8.21 | 57 |  | 163.48 | 3.51 | 6.85 | -5.019 | 0.29 | 101
8/5/2025 15:45 | 8 | 17 | 2.75 | 6.807 | 2.56 | 7.13 | 56 | 1.93 | 68.6 | 0.24 | 0.022 | 50.92 | 11182 | 8.21 | 57 |  | 164.85 | 3.49 | 6.86 | -5.019 | 0.28 | 101
8/5/2025 16:00 | 2 | 17 | 2.75 | 7.276 | 2.637 | 7.12 | 56 | 1.93 | 68.6 | 0.225 | 0.022 | 50.92 | 11182 | 8.21 | 57 |  | 177.15 | 3.51 | 6.85 | -5.019 | 0.28 | 101
8/5/2025 16:15 | 8 | 17 | 2.75 | 7.292 | 2.639 | 7.12 | 56 | 1.93 | 68.6 | 0.225 | 0.022 | 50.92 | 11182 | 8.19 | 57 |  | 176.73 | 3.49 | 6.85 | -5.019 | 0.29 | 101
8/5/2025 16:30 | 9 | 17 | 2.75 | 7.275 | 2.629 | 7.12 | 56 | 1.93 | 68.6 | 0.225 | 0.022 | 50.92 | 11182 | 8.17 | 57 |  | 176.7 | 3.5 | 6.85 | -5.019 | 0.29 | 101
8/5/2025 16:45 | 7 | 17 | 2.75 | 6.765 | 2.631 | 7.11 | 56 | 1.93 | 68.6 | 0.225 | 0.022 | 50.92 | 11182 | 8.17 | 57 |  | 163.66 | 3.48 | 6.85 | -5.019 | 0.29 | 101
8/5/2025 17:00 | 6 | 17 | 2.75 | 6.757 | 39.935 | 7.09 | 56 | 1.93 | 68.6 | 0.225 | 0.022 | 50.92 | 11182 | 8.19 | 57 |  | 0 | 0 | 6.85 | -5.019 | 0.41 | 101
8/5/2025 17:15 | -18 | 17 | 2.75 | 7.001 | 4.27 | 7.15 | 56 | 1.93 | 68.6 | 0.225 | 0.022 | 50.92 | 11182 | 8.21 | 57 |  | 0 | 0 | 6.84 | -5.019 | 0.29 | 91
8/5/2025 17:30 | 3 | 17 | 2.75 | 7.217 | 3.3 | 7.18 | 56 | 1.93 | 68.6 | 0.225 | 0.022 | 50.92 | 11182 | 8.23 | 57 |  | 73.78 | 1.47 | 6.82 | -5.019 | 0.3 | 101
8/5/2025 17:45 | 7 | 17 | 2.75 | 7.246 | 39.936 | 7.09 | 56 | 1.93 | 68.6 | 0.225 | 0.022 | 50.92 | 11182 | 8.25 | 57 |  | 176.64 | 3.51 | 6.84 | -5.019 | 0.39 | 101
8/5/2025 18:00 | -7 | 17 | 2.75 | 7.194 | 39.936 | 7.11 | 56 | 1.93 | 68.7 | 0.225 | 0.022 | 50.92 | 11182 | 8.26 | 57 |  | 175.54 | 3.51 | 6.84 | -5.019 | 0.32 | 101
8/5/2025 18:15 | 4 | 17 | 2.75 | 6.718 | 13.703 | 7.11 | 56 | 1.93 | 68.7 | 0.225 | 0.022 | 49.71 | 11170 | 8.27 | 57 |  | 162.31 | 3.48 | 6.85 | -5.019 | 0.3 | 101
8/5/2025 18:30 | 8 | 17 | 2.75 | 7.197 | 5.535 | 7.1 | 56 | 1.93 | 68.7 | 0.225 | 0.023 | 49.71 | 11170 | 8.27 | 57 |  | 173.16 | 3.46 | 6.84 | -5.019 | 0.3 | 101
8/5/2025 18:45 | 7 | 17 | 2.75 | 7.192 | 4.131 | 7.1 | 56 | 1.93 | 68.7 | 0.225 | 0.024 | 49.71 | 11170 | 8.28 | 57 |  | 175.66 | 3.52 | 6.82 | -5.019 | 0.3 | 101
8/5/2025 19:00 | 8 | 17 | 2.75 | 7.227 | 3.748 | 7.09 | 56 | 1.93 | 68.7 | 0.225 | 0.024 | 49.71 | 11170 | 8.29 | 57 |  | 175.77 | 3.5 | 6.82 | -5.019 | 0.29 | 101
8/5/2025 19:15 | -3 | 17 | 2.75 | 7.189 | 3.422 | 7.09 | 56 | 1.93 | 68.7 | 0.225 | 0.024 | 49.71 | 11170 | 8.29 | 57 |  | 175.03 | 3.51 | 6.82 | -5.019 | 0.29 | 101
8/5/2025 19:30 | 9 | 17 | 2.75 | 6.782 | 3.255 | 7.1 | 56 | 1.93 | 68.7 | 0.225 | 0.024 | 49.71 | 11170 | 8.28 | 57 |  | 164.97 | 3.5 | 6.82 | -5.019 | 0.3 | 101
8/5/2025 19:45 | 8 | 17 | 2.75 | 6.753 | 2.83 | 7.12 | 56 | 1.93 | 68.7 | 0.225 | 0.024 | 49.71 | 11170 | 8.27 | 57 |  | 164.75 | 3.51 | 6.84 | -5.019 | 0.3 | 101
8/5/2025 20:00 | 11 | 17 | 2.75 | 7.11 | 2.476 | 7.13 | 56 | 1.93 | 68.7 | 0.244 | 0.024 | 49.71 | 11170 | 8.28 | 57 |  | 173.7 | 3.52 | 6.85 | -5.019 | 0.29 | 101
8/5/2025 20:15 | 7 | 17 | 2.75 | 7.142 | 2.697 | 7.12 | 56 | 1.93 | 68.7 | 0.244 | 0.024 | 49.71 | 11170 | 8.3 | 57 |  | 173.17 | 3.49 | 6.85 | -5.019 | 0.27 | 101
8/5/2025 20:30 | 7 | 17 | 2.75 | 7.131 | 2.399 | 7.13 | 56 | 1.93 | 68.7 | 0.244 | 0.024 | 49.71 | 11170 | 8.32 | 57 |  | 173.47 | 3.5 | 6.83 | -5.019 | 0.29 | 101
8/5/2025 20:45 | 7 | 17 | 2.75 | 7.165 | 2.876 | 7.11 | 56 | 1.93 | 68.7 | 0.244 | 0.024 | 49.71 | 11170 | 8.33 | 57 |  | 173.86 | 3.49 | 6.82 | -5.019 | 0.3 | 101
8/5/2025 21:00 | 0 | 17 | 2.75 | 7.141 | 3.053 | 7.09 | 56 | 1.93 | 68.7 | 0.244 | 0.024 | 49.71 | 11170 | 8.34 | 57 |  | 173.95 | 3.51 | 6.8 | -5.019 | 0.29 | 101
8/5/2025 21:15 | 2 | 17 | 2.75 | 7.143 | 2.99 | 7.09 | 56 | 1.93 | 68.7 | 0.244 | 0.024 | 49.71 | 11170 | 8.34 | 57 |  | 173.6 | 3.5 | 6.79 | -5.019 | 0.3 | 101
8/5/2025 21:30 | 4 | 17 | 2.75 | 7.135 | 3.305 | 7.14 | 56 | 1.93 | 68.7 | 0.244 | 0.024 | 49.71 | 11170 | 8.34 | 57 |  | 0 | 0 | 6.79 | -5.019 | 0.3 | 101
8/5/2025 21:45 | 2 | 17 | 2.75 | 7.131 | 3.318 | 7.15 | 56 | 1.93 | 68.7 | 0.244 | 0.024 | 49.71 | 11170 | 8.33 | 57 |  | 0 | 0 | 6.8 | -5.019 | 0.3 | 101
8/5/2025 22:00 | 0 | 17 | 2.75 | 7.135 | 3.253 | 7.15 | 59 | 1.93 | 68.5 | 0.244 | 0.024 | 49.71 | 11170 | 8.32 | 57 |  | 0 | 0 | 6.81 | -5.019 | 0.31 | 101
8/5/2025 22:15 | -1 | 17 | 2.75 | 7.144 | 3.266 | 7.16 | 59 | 1.93 | 68.5 | 0.244 | 0.024 | 49.71 | 11170 | 8.31 | 57 |  | 0 | 0 | 6.82 | -5.019 | 0.29 | 101
8/5/2025 22:30 | 3 | 17 | 2.75 | 7.101 | 3.243 | 7.16 | 59 | 1.93 | 68.5 | 0.244 | 0.024 | 49.71 | 11170 | 8.31 | 57 |  | 0 | 0 | 6.82 | -5.019 | 0.3 | 101
8/5/2025 22:45 | 1 | 17 | 2.75 | 6.986 | 3.106 | 7.16 | 59 | 1.93 | 68.5 | 0.244 | 0.024 | 49.71 | 11170 | 8.3 | 57 |  | 0 | 0 | 6.82 | -5.019 | 0.3 | 101
8/5/2025 23:00 | 3 | 17 | 2.75 | 6.949 | 3.069 | 7.17 | 59 | 1.93 | 68.5 | 0.244 | 0.024 | 49.71 | 11170 | 8.3 | 57 |  | 0 | 0 | 6.83 | -5.019 | 0.28 | 101
8/5/2025 23:15 | 0 | 17 | 2.75 | 7.139 | 3.457 | 7.11 | 59 | 1.93 | 68.5 | 0.244 | 0.023 | 49.71 | 11170 | 8.3 | 57 |  | 172.88 | 3.49 | 6.82 | -5.019 | 0.28 | 101
8/5/2025 23:30 | -1 | 17 | 2.75 | 7.356 | 3.784 | 7.1 | 59 | 1.93 | 68.5 | 0.244 | 0.023 | 49.71 | 11170 | 8.3 | 57 |  | 177.93 | 3.48 | 6.8 | -5.019 | 0.28 | 101
8/5/2025 23:45 | 1 | 17 | 2.75 | 7.355 | 3.409 | 7.1 | 59 | 1.93 | 68.5 | 0.244 | 0.023 | 49.71 | 11170 | 8.3 | 57 |  | 179.15 | 3.51 | 6.81 | -5.019 | 0.28 | 101
8/6/2025 00:00 | -6 | 17 | 2.75 | 7.304 | 3.111 | 7.1 | 59 | 1.93 | 68.5 | 0.346 | 0.023 | 49.71 | 11170 | 8.3 | 57 |  | 177.94 | 3.51 | 6.8 | -5.019 | 0.28 | 101
8/6/2025 00:15 | 2 | 17 | 2.75 | 7.25 | 2.899 | 7.1 | 59 | 1.93 | 68.5 | 0.346 | 0.023 | 48.75 | 11123 | 8.31 | 57 |  | 177.34 | 3.52 | 6.81 | -5.019 | 0.3 | 101
8/6/2025 00:30 | 6 | 17 | 2.75 | 7.447 | 2.649 | 7.11 | 59 | 1.93 | 68.5 | 0.346 | 0.023 | 48.75 | 11123 | 8.31 | 57 |  | 180.08 | 3.48 | 6.83 | -5.019 | 0.3 | 101
8/6/2025 00:45 | 7 | 17 | 2.75 | 7.447 | 2.583 | 7.12 | 59 | 1.93 | 68.5 | 0.346 | 0.024 | 48.75 | 11123 | 8.31 | 57 |  | 180.54 | 3.49 | 6.84 | -5.019 | 0.29 | 101
8/6/2025 01:00 | 1 | 17 | 2.75 | 7.445 | 2.632 | 7.11 | 59 | 1.93 | 68.5 | 0.346 | 0.024 | 48.75 | 11123 | 8.31 | 57 |  | 180.68 | 3.49 | 6.86 | -5.019 | 0.28 | 101
8/6/2025 01:15 | 0 | 17 | 2.75 | 7.44 | 2.749 | 7.11 | 59 | 1.93 | 68.5 | 0.346 | 0.024 | 48.75 | 11123 | 8.31 | 57 |  | 180.24 | 3.49 | 6.87 | -5.019 | 0.3 | 101
8/6/2025 01:30 | 1 | 17 | 2.75 | 7.408 | 2.616 | 7.11 | 59 | 1.93 | 68.5 | 0.346 | 0.024 | 48.75 | 11123 | 8.3 | 57 |  | 180.17 | 3.5 | 6.86 | -5.019 | 0.28 | 101
8/6/2025 01:45 | 8 | 17 | 2.75 | 7.728 | 2.685 | 7.11 | 59 | 1.93 | 68.5 | 0.346 | 0.024 | 48.75 | 11123 | 8.29 | 57 |  | 180.45 | 3.36 | 6.86 | -5.019 | 0.28 | 101
8/6/2025 02:00 | 4 | 17 | 2.75 | 7.758 | 2.814 | 7.1 | 59 | 1.93 | 68.3 | 0.346 | 0.024 | 48.75 | 11123 | 8.31 | 57 |  | 180.19 | 3.34 | 6.85 | -5.019 | 0.26 | 101
8/6/2025 02:15 | 0 | 17 | 2.75 | 7.796 | 2.888 | 7.1 | 59 | 1.93 | 68.3 | 0.346 | 0.024 | 48.75 | 11123 | 8.34 | 57 |  | 179.99 | 3.32 | 6.85 | -5.019 | 0.26 | 101
8/6/2025 02:30 | 0 | 17 | 2.75 | 7.8 | 2.896 | 7.09 | 59 | 1.93 | 68.3 | 0.346 | 0.024 | 48.75 | 11123 | 8.36 | 57 |  | 180.47 | 3.33 | 6.84 | -5.019 | 0.29 | 101
8/6/2025 02:45 | 2 | 17 | 2.75 | 7.752 | 2.93 | 7.09 | 59 | 1.93 | 68.3 | 0.346 | 0.024 | 48.75 | 11123 | 8.36 | 57 |  | 180.05 | 3.34 | 6.84 | -5.019 | 0.29 | 101
8/6/2025 03:00 | 2 | 17 | 2.75 | 7.774 | 2.828 | 7.09 | 59 | 1.93 | 68.3 | 0.346 | 0.024 | 48.75 | 11123 | 8.36 | 57 |  | 180.09 | 3.34 | 6.84 | -5.019 | 0.27 | 101
8/6/2025 03:15 | 1 | 17 | 2.75 | 7.981 | 2.815 | 7.09 | 59 | 1.93 | 68.3 | 0.346 | 0.024 | 48.75 | 11123 | 8.35 | 57 |  | 180.47 | 3.26 | 6.83 | -5.019 | 0.28 | 101
8/6/2025 03:30 | 1 | 17 | 2.75 | 7.988 | 2.744 | 7.09 | 59 | 1.93 | 68.3 | 0.346 | 0.024 | 48.75 | 11123 | 8.35 | 57 |  | 180.13 | 3.25 | 6.82 | -5.019 | 0.29 | 101
8/6/2025 03:45 | 7 | 17 | 2.75 | 7.995 | 2.673 | 7.09 | 59 | 1.93 | 68.3 | 0.346 | 0.024 | 48.75 | 11123 | 8.35 | 57 |  | 180.18 | 3.25 | 6.81 | -5.019 | 0.27 | 101
8/6/2025 04:00 | 6 | 17 | 2.75 | 7.443 | 2.654 | 7.09 | 59 | 1.93 | 68.3 | 0.402 | 0.024 | 48.75 | 11123 | 8.35 | 57 |  | 179.74 | 3.48 | 6.8 | -5.019 | 0.29 | 101
8/6/2025 04:15 | 7 | 17 | 2.75 | 7.472 | 2.6 | 7.1 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.35 | 57 |  | 0 | 0 | 6.8 | -5.019 | 0.28 | 101
8/6/2025 04:30 | 5 | 17 | 2.75 | 8.101 | 2.931 | 7.12 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.35 | 57 |  | 0 | 0 | 6.81 | -5.019 | 0.31 | 101
8/6/2025 04:45 | 2 | 17 | 2.75 | 8.137 | 3.04 | 7.12 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.34 | 57 |  | 0 | 0 | 6.8 | -5.019 | 0.31 | 101
8/6/2025 05:00 | 5 | 17 | 2.75 | 8.145 | 3.225 | 7.12 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.34 | 57 |  | 0 | 0 | 6.8 | -5.019 | 0.28 | 101
8/6/2025 05:15 | 0 | 17 | 2.75 | 8.129 | 3.619 | 7.12 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.34 | 57 |  | 178.39 | 3.16 | 6.8 | -5.019 | 0.26 | 101
8/6/2025 05:30 | 4 | 17 | 2.75 | 8.081 | 15.83 | 7.09 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.34 | 57 |  | 177.73 | 3.17 | 6.79 | -5.019 | 0.32 | 101
8/6/2025 05:45 | -2 | 17 | 2.75 | 7.583 | 4.011 | 7.08 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.33 | 57 |  | 177.67 | 3.37 | 6.79 | -5.019 | 0.29 | 101
8/6/2025 06:00 | 8 | 17 | 2.75 | 7.784 | 3.354 | 7.08 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.33 | 57 |  | 177.84 | 3.29 | 6.8 | -5.019 | 0.28 | 101
8/6/2025 06:15 | 5 | 17 | 2.75 | 8.043 | 3.145 | 7.08 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.33 | 57 |  | 177.13 | 3.17 | 6.79 | -5.019 | 0.29 | 101
8/6/2025 06:30 | 9 | 17 | 2.75 | 8.604 | 3.521 | 7.07 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.33 | 57 |  | 177.23 | 2.97 | 6.78 | -5.019 | 0.3 | 101
8/6/2025 06:45 | 6 | 17 | 2.75 | 8.61 | 3.424 | 7.07 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.33 | 57 |  | 176.86 | 2.96 | 6.76 | -5.019 | 0.29 | 101
8/6/2025 07:00 | 6 | 17 | 2.75 | 8.579 | 3.154 | 7.07 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.32 | 57 |  | 176.9 | 2.97 | 6.77 | -5.019 | 0.3 | 101
8/6/2025 07:15 | -4 | 17 | 2.75 | 7.841 | 3.053 | 7.07 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.32 | 57 |  | 176.79 | 3.25 | 6.76 | -5.019 | 0.3 | 101
8/6/2025 07:30 | 4 | 17 | 2.75 | 7.879 | 2.9 | 7.07 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.32 | 57 |  | 177.21 | 3.24 | 6.78 | -5.019 | 0.3 | 101
8/6/2025 07:45 | 0 | 17 | 2.75 | 8.55 | 2.908 | 7.08 | 59 | 1.93 | 68.3 | 0.402 | 0.023 | 48.75 | 11123 | 8.31 | 57 |  | 177.07 | 2.98 | 6.78 | -5.019 | 0.28 | 101
8/6/2025 08:00 | -1 | 17 | 2.75 | 8.769 | 2.966 | 7.08 | 59 | 1.93 | 68.3 | 0.43 | 0.023 | 48.75 | 11123 | 8.31 | 57 |  | 177.67 | 2.92 | 6.78 | -5.019 | 0.29 | 101
8/6/2025 08:15 | 0 | 17 | 2.75 | 8.772 | 2.9 | 7.08 | 59 | 1.93 | 68.3 | 0.43 | 0.023 | 48.75 | 11123 | 8.31 | 57 |  | 177.33 | 2.91 | 6.78 | -5.019 | 0.27 | 101
8/6/2025 08:30 | -1 | 17 | 2.75 | 9.035 | 2.915 | 7.08 | 59 | 1.93 | 68.3 | 0.43 | 0.023 | 48.75 | 11123 | 8.31 | 57 |  | 177.29 | 2.83 | 6.77 | -5.019 | 0.27 | 101
8/6/2025 08:45 | 2 | 17 | 2.75 | 9.039 | 2.903 | 7.08 | 59 | 1.93 | 68.3 | 0.43 | 0.023 | 48.75 | 11123 | 8.31 | 57 |  | 176.89 | 2.82 | 6.77 | -5.019 | 0.29 | 101
8/6/2025 09:00 | 4 | 17 | 2.75 | 9.093 | 2.87 | 7.08 | 59 | 1.93 | 68.3 | 0.43 | 0.023 | 48.75 | 11123 | 8.31 | 57 |  | 176.93 | 2.8 | 6.76 | -5.019 | 0.31 | 101
8/6/2025 09:15 | 2 | 17 | 2.75 | 9.083 | 2.898 | 7.09 | 59 | 1.93 | 68.3 | 0.43 | 0.023 | 48.75 | 11123 | 8.3 | 57 |  | 125.95 | 2 | 6.76 | -5.019 | 0.29 | 101
8/6/2025 09:30 | 0 | 17 | 2.75 | 9.063 | 2.938 | 7.09 | 59 | 1.93 | 68.3 | 0.43 | 0.023 | 48.75 | 11123 | 8.29 | 57 |  | 126.01 | 2 | 6.75 | -5.019 | 0.28 | 101
8/6/2025 09:45 | -7 | 17 | 2.75 | 9.013 | 3.07 | 7.09 | 59 | 1.93 | 68.3 | 0.43 | 0.022 | 48.75 | 11123 | 8.28 | 57 |  | 125.54 | 2.01 | 6.74 | -5.019 | 0.28 | 101
8/6/2025 10:00 | -8 | 17 | 2.75 | 8.625 | 3.137 | 7.09 | 56 | 1.93 | 68.5 | 0.43 | 0.023 | 48.75 | 11123 | 8.26 | 57 |  | 120.18 | 2.01 | 6.74 | -5.019 | 0.29 | 101
8/6/2025 10:15 | -5 | 19 | 2.75 | 8.616 | 3.203 | 7.09 | 56 | 1.93 | 68.5 | 0.43 | 0.022 | 48.75 | 11123 | 8.25 | 57 |  | 119.51 | 2 | 6.73 | -5.019 | 0.28 | 101
8/6/2025 10:30 | 5 | 19 | 2.75 | 9.22 | 3.345 | 7.09 | 56 | 1.93 | 68.5 | 0.43 | 0.022 | 48.75 | 11123 | 8.25 | 57 |  | 94.52 | 1.48 | 6.73 | -5.019 | 0.27 | 101
8/6/2025 10:45 | 10 | 19 | 2.75 | 9.236 | 3.272 | 7.1 | 56 | 1.93 | 68.5 | 0.43 | 0.022 | 48.75 | 11123 | 8.25 | 57 |  | 95.78 | 1.49 | 6.72 | -5.019 | 0.28 | 101
8/6/2025 11:00 | 9 | 19 | 2.75 | 9.247 | 3.389 | 7.1 | 56 | 1.93 | 68.5 | 0.43 | 0.022 | 48.75 | 11123 | 8.25 | 57 |  | 95.91 | 1.49 | 6.72 | -5.019 | 0.28 | 101
8/6/2025 11:15 | 8 | 19 | 2.75 | 9.199 | 3.356 | 7.11 | 56 | 1.93 | 68.5 | 0.43 | 0.022 | 48.75 | 11123 | 8.25 | 57 |  | 95.85 | 1.5 | 6.71 | -5.019 | 0.26 | 101
8/6/2025 11:30 | 10 | 19 | 2.75 | 8.681 | 3.256 | 7.11 | 56 | 1.93 | 68.5 | 0.43 | 0.022 | 48.75 | 11123 | 8.25 | 57 |  | 90.83 | 1.51 | 6.71 | -5.019 | 0.27 | 101
8/6/2025 11:45 | 8 | 19 | 2.75 | 8.685 | 3.119 | 7.11 | 56 | 1.93 | 68.5 | 0.43 | 0.022 | 48.75 | 11123 | 8.25 | 57 |  | 90.53 | 1.5 | 6.71 | -5.019 | 0.26 | 101
8/6/2025 12:00 | 12 | 19 | 2.75 | 9.067 | 39.934 | 7.17 | 56 | 1.93 | 68.5 | 0.296 | 0.022 | 48.75 | 11123 | 8.25 | 57 |  | 94.35 | 1.5 | 6.79 | -4.214 | 0.31 | 94
8/6/2025 12:15 | 18 | 19 | 2.75 | 9.082 | 2.526 | 7.09 | 56 | 1.93 | 68.5 | 0.296 | 0.022 | 48.75 | 11123 | 8.25 | 57 |  | 94.5 | 1.5 | 6.78 | -4.214 | 0.28 | 93
8/6/2025 12:30 | 23 | 19 | 2.75 | 9.029 | 2.368 | 7.12 | 56 | 1.93 | 68.5 | 0.296 | 0.022 | 48.75 | 11123 | 8.24 | 57 |  | 94.35 | 1.5 | 6.83 | -4.214 | 0.29 | 87
8/6/2025 12:45 | 22 | 19 | 2.75 | 9.033 | 2.326 | 7.13 | 56 | 1.93 | 68.5 | 0.296 | 0.022 | 48.75 | 11123 | 8.24 | 57 |  | 94.57 | 1.51 | 6.88 | -4.214 | 0.28 | 89
8/6/2025 13:00 | 22 | 19 | 2.75 | 8.474 | 2.285 | 7.13 | 56 | 1.93 | 68.5 | 0.296 | 0.022 | 48.75 | 11123 | 8.24 | 57 |  | 88.65 | 1.51 | 6.88 | -4.214 | 0.29 | 88
8/6/2025 13:15 | 22 | 19 | 2.75 | 8.775 | 2.34 | 7.13 | 56 | 1.93 | 68.5 | 0.296 | 0.022 | 48.75 | 11123 | 8.23 | 57 |  | 92.07 | 1.51 | 6.86 | -4.214 | 0.33 | 86
8/6/2025 13:30 | 22 | 19 | 2.75 | 8.848 | 2.645 | 7.13 | 56 | 1.93 | 68.5 | 0.296 | 0.022 | 48.75 | 11123 | 8.21 | 57 |  | 92.18 | 1.5 | 6.86 | -4.214 | 0.31 | 87
8/6/2025 13:45 | 24 | 19 | 2.75 | 8.834 | 2.268 | 7.14 | 56 | 1.93 | 68.5 | 0.296 | 0.022 | 48.75 | 11123 | 8.19 | 57 |  | 92.23 | 1.5 | 6.87 | -4.214 | 0.33 | 87
8/6/2025 14:00 | 22 | 19 | 2.75 | 8.813 | 2.672 | 7.12 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 48.75 | 11123 | 8.19 | 59 |  | 92.32 | 1.51 | 6.83 | -4.214 | 0.32 | 88
8/6/2025 14:15 | 21 | 19 | 2.75 | 8.815 | 2.83 | 7.11 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 48.75 | 11123 | 8.2 | 59 |  | 92.68 | 1.51 | 6.83 | -4.214 | 0.31 | 87
8/6/2025 14:30 | 22 | 19 | 2.75 | 8.838 | 2.708 | 7.12 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 48.75 | 11123 | 8.21 | 59 |  | 92.53 | 1.51 | 6.84 | -4.214 | 0.32 | 89
8/6/2025 14:45 | 21 | 19 | 2.75 | 8.852 | 2.691 | 7.13 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 48.75 | 11123 | 8.21 | 59 |  | 92.07 | 1.5 | 6.85 | -4.214 | 0.36 | 88
8/6/2025 15:00 | 25 | 19 | 2.75 | 8.818 | 2.991 | 7.13 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 48.75 | 11123 | 8.2 | 59 |  | 61.63 | 1.01 | 6.83 | -4.214 | 0.31 | 85
8/6/2025 15:15 | 18 | 19 | 2.75 | 8.877 | 2.62 | 7.14 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 48.75 | 11123 | 8.2 | 59 |  | 61.77 | 1 | 6.86 | -4.214 | 0.31 | 89
8/6/2025 15:30 | 22 | 19 | 2.75 | 8.858 | 2.728 | 7.16 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 48.75 | 11123 | 8.19 | 59 |  | 61.61 | 1 | 6.86 | -4.214 | 0.31 | 87
8/6/2025 15:45 | 23 | 19 | 2.75 | 8.843 | 2.795 | 7.15 | 56 | 1.93 | 68.7 | 0.296 | 0.021 | 48.75 | 11123 | 8.18 | 59 |  | 61.76 | 1.01 | 6.85 | -4.214 | 0.31 | 86
8/6/2025 16:00 | 24 | 19 | 2.75 | 8.808 | 2.804 | 7.15 | 56 | 1.93 | 68.7 | 0.296 | 0.021 | 48.75 | 11123 | 8.17 | 59 |  | 61.45 | 1 | 6.84 | -4.214 | 0.31 | 86
8/6/2025 16:15 | 22 | 19 | 2.75 | 8.831 | 2.916 | 7.14 | 56 | 1.93 | 68.7 | 0.296 | 0.021 | 48.75 | 11123 | 8.17 | 59 |  | 61.31 | 1 | 6.84 | -4.214 | 0.32 | 86
8/6/2025 16:30 | 24 | 19 | 2.75 | 8.828 | 2.798 | 7.14 | 56 | 1.93 | 68.7 | 0.296 | 0.021 | 48.75 | 11123 | 8.16 | 59 |  | 61.47 | 1 | 6.84 | -4.214 | 0.32 | 84
8/6/2025 16:45 | 25 | 19 | 2.75 | 8.832 | 2.782 | 7.16 | 56 | 1.93 | 68.7 | 0.296 | 0.021 | 48.75 | 11123 | 8.15 | 59 |  | 61.44 | 1 | 6.85 | -4.214 | 0.3 | 83
8/6/2025 17:00 | 18 | 19 | 2.75 | 8.956 | 3.043 | 7.14 | 56 | 1.93 | 68.7 | 0.296 | 0.021 | 48.75 | 11123 | 8.14 | 59 |  | 61.46 | 0.99 | 6.83 | -4.214 | 0.33 | 92
8/6/2025 17:15 | 19 | 19 | 2.75 | 8.958 | 3.4 | 7.12 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 48.75 | 11123 | 8.14 | 59 |  | 62.13 | 1 | 6.79 | -4.214 | 0.32 | 89
8/6/2025 17:30 | 12 | 19 | 2.75 | 7.86 | 3.651 | 7.1 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 48.75 | 11123 | 8.13 | 59 |  | 55.09 | 1.01 | 6.79 | -4.214 | 0.34 | 93
8/6/2025 17:45 | 23 | 19 | 2.75 | 8 | 3.492 | 7.12 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 45.16 | 10494 | 8.13 | 59 |  | 55.14 | 0.99 | 6.81 | -4.214 | 0.33 | 86
8/6/2025 18:00 | 23 | 19 | 2.75 | 8.18 | 3.389 | 7.13 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 45.16 | 10494 | 8.12 | 59 |  | 56.68 | 1 | 6.83 | -4.214 | 0.32 | 86
8/6/2025 18:15 | 24 | 19 | 2.75 | 8.178 | 3.217 | 7.14 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 45.16 | 10494 | 8.12 | 59 |  | 56.91 | 1 | 6.84 | -4.214 | 0.32 | 86
8/6/2025 18:30 | 23 | 19 | 2.75 | 7.41 | 2.962 | 7.16 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 45.16 | 10494 | 8.12 | 59 |  | 0 | 0 | 6.86 | -4.214 | 0.31 | 85
8/6/2025 18:45 | 22 | 19 | 2.75 | 7.425 | 3.085 | 7.16 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 45.16 | 10494 | 8.1 | 59 |  | 0 | 0 | 6.87 | -4.214 | 0.31 | 87
8/6/2025 19:00 | 21 | 19 | 2.75 | 7.722 | 3.251 | 7.15 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 45.16 | 10494 | 8.09 | 59 |  | 0 | 0 | 6.86 | -4.214 | 0.31 | 88
8/6/2025 19:15 | 21 | 19 | 2.75 | 7.684 | 3.222 | 7.16 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 45.16 | 10494 | 8.1 | 59 |  | 0 | 0 | 6.86 | -4.214 | 0.32 | 88
8/6/2025 19:30 | 21 | 19 | 2.75 | 7.698 | 3.295 | 7.16 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 45.16 | 10494 | 8.13 | 59 |  | 0 | 0 | 6.86 | -4.214 | 0.33 | 89
8/6/2025 19:45 | 21 | 19 | 2.75 | 7.693 | 3.415 | 7.15 | 56 | 1.93 | 68.7 | 0.296 | 0.022 | 45.16 | 10494 | 8.14 | 59 |  | 0 | 0 | 6.85 | -4.214 | 0.32 | 89
8/6/2025 20:00 | 19 | 19 | 2.75 | 7.721 | 3.81 | 7.14 | 56 | 1.93 | 68.7 | 0.421 | 0.022 | 45.16 | 10494 | 8.15 | 59 |  | 0 | 0 | 6.83 | -4.214 | 0.28 | 90
8/6/2025 20:15 | 14 | 19 | 2.75 | 7.967 | 3.647 | 7.13 | 56 | 1.93 | 68.7 | 0.421 | 0.022 | 45.16 | 10494 | 8.15 | 59 |  | 0 | 0 | 6.82 | -4.214 | 0.34 | 94
8/6/2025 20:30 | 18 | 19 | 2.75 | 7.963 | 3.304 | 7.12 | 56 | 1.93 | 68.7 | 0.421 | 0.021 | 45.16 | 10494 | 8.15 | 59 |  | 165.77 | 3 | 6.83 | -4.214 | 0.32 | 90
8/6/2025 20:45 | 14 | 19 | 2.75 | 7.95 | 3.271 | 7.13 | 56 | 1.93 | 68.7 | 0.421 | 0.021 | 45.16 | 10494 | 8.15 | 59 |  | 165.65 | 3 | 6.83 | -4.214 | 0.32 | 93
8/6/2025 21:00 | 26 | 19 | 2.75 | 7.938 | 3.023 | 7.12 | 56 | 1.93 | 68.7 | 0.421 | 0.022 | 45.16 | 10494 | 8.15 | 59 |  | 166.05 | 3.01 | 6.83 | -4.214 | 0.32 | 84
8/6/2025 21:15 | 21 | 19 | 2.75 | 7.34 | 3.023 | 7.12 | 56 | 1.93 | 68.7 | 0.421 | 0.021 | 45.16 | 10494 | 8.15 | 59 |  | 151.89 | 2.98 | 6.83 | -4.214 | 0.3 | 86
8/6/2025 21:30 | 20 | 19 | 2.75 | 7.512 | 3.166 | 7.11 | 56 | 1.93 | 68.7 | 0.421 | 0.021 | 45.16 | 10494 | 8.15 | 59 |  | 156.38 | 3 | 6.82 | -4.214 | 0.3 | 87
8/6/2025 21:45 | 17 | 19 | 2.75 | 7.777 | 3.149 | 7.12 | 56 | 1.93 | 68.7 | 0.421 | 0.021 | 45.16 | 10494 | 8.14 | 59 |  | 162.24 | 3 | 6.82 | -4.214 | 0.3 | 91
8/6/2025 22:00 | 21 | 19 | 2.75 | 7.775 | 2.995 | 7.12 | 57 | 1.93 | 68.7 | 0.421 | 0.021 | 45.16 | 10494 | 8.14 | 59 |  | 162.38 | 3.01 | 6.83 | -4.214 | 0.29 | 88
8/6/2025 22:15 | 20 | 19 | 2.75 | 8.034 | 2.709 | 7.12 | 57 | 1.93 | 68.7 | 0.421 | 0.021 | 45.16 | 10494 | 8.14 | 59 |  | 167.33 | 3 | 6.83 | -4.214 | 0.29 | 88
8/6/2025 22:30 | 21 | 19 | 2.75 | 8.003 | 2.506 | 7.13 | 57 | 1.93 | 68.7 | 0.421 | 0.021 | 45.16 | 10494 | 8.14 | 59 |  | 168.08 | 3.02 | 6.84 | -4.214 | 0.29 | 86
8/6/2025 22:45 | 20 | 19 | 2.75 | 8.064 | 2.596 | 7.13 | 57 | 1.93 | 68.7 | 0.421 | 0.021 | 42.47 | 9853 | 8.13 | 59 |  | 167.22 | 2.99 | 6.84 | -4.214 | 0.3 | 89
8/6/2025 23:00 | 17 | 19 | 2.75 | 8.02 | 2.701 | 7.12 | 57 | 1.93 | 68.7 | 0.421 | 0.022 | 42.47 | 9853 | 8.13 | 59 |  | 166.81 | 3 | 6.84 | -4.214 | 0.28 | 90
8/6/2025 23:15 | 6 | 19 | 2.75 | 7.631 | 3.065 | 7.11 | 57 | 1.93 | 68.7 | 0.421 | 0.023 | 42.47 | 9853 | 8.12 | 59 |  | 158.65 | 2.99 | 6.82 | -4.214 | 0.27 | 101
8/6/2025 23:30 | 13 | 19 | 2.75 | 7.722 | 2.97 | 7.11 | 57 | 1.93 | 68.7 | 0.421 | 0.023 | 42.47 | 9853 | 8.12 | 59 |  | 159.81 | 2.98 | 6.83 | -4.214 | 0.26 | 92
8/6/2025 23:45 | 11 | 19 | 2.75 | 7.791 | 2.957 | 7.11 | 57 | 1.93 | 68.7 | 0.421 | 0.022 | 42.47 | 9853 | 8.11 | 59 |  | 162 | 2.99 | 6.83 | -4.214 | 0.3 | 92
8/7/2025 00:00 | 14 | 19 | 2.75 | 7.76 | 2.91 | 7.11 | 57 | 1.98 | 68.7 | 0.378 | 0.023 | 42.47 | 9853 | 8.09 | 59 |  | 162.02 | 3.01 | 6.84 | -4.214 | 0.3 | 92
8/7/2025 00:15 | 14 | 19 | 2.75 | 7.799 | 2.818 | 7.11 | 57 | 1.98 | 68.7 | 0.378 | 0.022 | 42.47 | 9853 | 8.09 | 59 |  | 162.54 | 3 | 6.84 | -4.214 | 0.29 | 92
8/7/2025 00:30 | 10 | 19 | 2.75 | 7.829 | 2.863 | 7.11 | 57 | 1.98 | 68.7 | 0.378 | 0.022 | 42.47 | 9853 | 8.12 | 59 |  | 162.25 | 2.98 | 6.83 | -4.214 | 0.29 | 101
8/7/2025 00:45 | -3 | 19 | 2.75 | 7.841 | 2.662 | 7.11 | 57 | 1.98 | 68.7 | 0.378 | 0.022 | 42.47 | 9853 | 8.14 | 59 |  | 162.73 | 2.99 | 6.83 | -4.214 | 0.3 | 101
8/7/2025 01:00 | 10 | 19 | 2.75 | 7.784 | 2.592 | 7.12 | 57 | 1.98 | 68.7 | 0.378 | 0.022 | 40.35 | 9529 | 8.15 | 59 |  | 162.49 | 3.01 | 6.84 | -4.214 | 0.3 | 101
8/7/2025 01:15 | 15 | 19 | 2.75 | 7.775 | 2.463 | 7.12 | 57 | 1.98 | 68.7 | 0.378 | 0.023 | 40.35 | 9529 | 8.14 | 59 |  | 162.21 | 3 | 6.84 | -4.214 | 0.26 | 91
8/7/2025 01:30 | 10 | 19 | 2.75 | 7.468 | 2.461 | 7.12 | 57 | 1.98 | 68.7 | 0.378 | 0.023 | 40.35 | 9529 | 8.13 | 59 |  | 0 | 0 | 6.85 | -4.214 | 0.3 | 101
8/7/2025 01:45 | 12 | 19 | 2.75 | 7.362 | 2.778 | 7.12 | 57 | 1.98 | 68.7 | 0.378 | 0.023 | 40.35 | 9529 | 8.12 | 59 |  | 177.33 | 3.47 | 6.84 | -4.214 | 0.29 | 92
8/7/2025 02:00 | 12 | 19 | 2.75 | 7.635 | 4.445 | 7.1 | 57 | 1.98 | 68.5 | 0.378 | 0.023 | 40.35 | 9529 | 8.1 | 58 |  | 177.24 | 3.34 | 6.83 | -4.214 | 0.28 | 101
8/7/2025 02:15 | 11 | 19 | 2.75 | 7.659 | 3.473 | 7.08 | 57 | 1.98 | 68.5 | 0.378 | 0.023 | 40.35 | 9529 | 8.07 | 58 |  | 177.53 | 3.34 | 6.82 | -4.214 | 0.46 | 101
8/7/2025 02:30 | 10 | 19 | 2.75 | 7.643 | 3.305 | 7.08 | 57 | 1.98 | 68.5 | 0.378 | 0.023 | 40.35 | 9529 | 8.06 | 58 |  | 177.39 | 3.34 | 6.8 | -4.214 | 0.3 | 101
8/7/2025 02:45 | 7 | 19 | 2.75 | 7.641 | 3.057 | 7.08 | 57 | 1.98 | 68.5 | 0.378 | 0.023 | 40.35 | 9529 | 8.09 | 58 |  | 177.23 | 3.34 | 6.8 | -4.214 | 0.29 | 101
8/7/2025 03:00 | -4 | 19 | 2.75 | 7.869 | 2.853 | 7.08 | 57 | 1.98 | 68.5 | 0.378 | 0.023 | 40.35 | 9529 | 8.11 | 58 |  | 177.63 | 3.25 | 6.81 | -4.214 | 0.28 | 101
8/7/2025 03:15 | 6 | 19 | 2.75 | 7.821 | 2.647 | 7.09 | 57 | 1.98 | 68.5 | 0.378 | 0.023 | 40.35 | 9529 | 8.12 | 58 |  | 177.27 | 3.26 | 6.81 | -4.214 | 0.36 | 101
8/7/2025 03:30 | 13 | 19 | 2.75 | 7.808 | 2.526 | 7.09 | 57 | 1.98 | 68.5 | 0.378 | 0.023 | 40.35 | 9529 | 8.12 | 58 |  | 177.42 | 3.27 | 6.81 | -4.214 | 0.28 | 93
8/7/2025 03:45 | 11 | 19 | 2.75 | 7.835 | 2.603 | 7.09 | 57 | 1.98 | 68.5 | 0.378 | 0.023 | 40.35 | 9529 | 8.12 | 58 |  | 177.38 | 3.26 | 6.81 | -4.214 | 0.29 | 93
8/7/2025 04:00 | 10 | 19 | 2.75 | 7.884 | 2.904 | 7.08 | 57 | 1.98 | 68.5 | 0.387 | 0.023 | 40.35 | 9529 | 8.11 | 58 |  | 176.47 | 3.22 | 6.79 | -4.214 | 0.27 | 101
8/7/2025 04:15 | 8 | 19 | 2.75 | 7.851 | 2.723 | 7.08 | 57 | 1.98 | 68.5 | 0.387 | 0.023 | 38.67 | 9402 | 8.1 | 58 |  | 177.13 | 3.25 | 6.81 | -4.214 | 0.28 | 101
8/7/2025 04:30 | 10 | 19 | 2.75 | 7.849 | 2.772 | 7.08 | 57 | 1.98 | 68.5 | 0.387 | 0.023 | 38.67 | 9402 | 8.09 | 58 |  | 177.04 | 3.25 | 6.81 | -4.214 | 0.33 | 101
8/7/2025 04:45 | 8 | 19 | 2.75 | 8.096 | 2.695 | 7.08 | 57 | 1.98 | 68.5 | 0.387 | 0.024 | 38.67 | 9402 | 8.08 | 58 |  | 176.85 | 3.15 | 6.81 | -4.214 | 0.3 | 101
8/7/2025 05:00 | 11 | 19 | 2.75 | 8.077 | 2.609 | 7.09 | 57 | 1.98 | 68.5 | 0.387 | 0.024 | 38.67 | 9402 | 8.08 | 58 |  | 176.84 | 3.15 | 6.81 | -4.214 | 0.3 | 94
8/7/2025 05:15 | 14 | 19 | 2.75 | 8.139 | 2.619 | 7.09 | 57 | 1.98 | 68.5 | 0.387 | 0.024 | 38.67 | 9402 | 8.07 | 58 |  | 176.88 | 3.13 | 6.82 | -4.214 | 0.3 | 92
8/7/2025 05:30 | -2 | 19 | 2.75 | 8.096 | 2.588 | 7.09 | 57 | 1.98 | 68.5 | 0.387 | 0.024 | 38.67 | 9402 | 8.06 | 58 |  | 177.15 | 3.15 | 6.84 | -4.214 | 0.3 | 101
8/7/2025 05:45 | 12 | 19 | 2.75 | 8.11 | 2.521 | 7.09 | 57 | 1.98 | 68.5 | 0.387 | 0.024 | 38.67 | 9402 | 8.07 | 58 |  | 176.85 | 3.14 | 6.84 | -4.214 | 0.3 | 94
8/7/2025 06:00 | 13 | 19 | 2.75 | 8.385 | 2.917 | 7.1 | 57 | 1.98 | 68.5 | 0.387 | 0.024 | 38.67 | 9402 | 8.11 | 58 |  | 0 | 0 | 6.85 | -4.214 | 0.32 | 92
8/7/2025 06:15 | 7 | 19 | 2.75 | 8.373 | 2.933 | 7.12 | 57 | 1.98 | 68.5 | 0.387 | 0.024 | 38.67 | 9402 | 8.14 | 58 |  | 0 | 0 | 6.86 | -4.214 | 0.3 | 101
8/7/2025 06:30 | 8 | 19 | 2.75 | 8.345 | 2.7 | 7.11 | 57 | 1.98 | 68.5 | 0.387 | 0.023 | 38.67 | 9402 | 8.15 | 58 |  | 180.4 | 3.11 | 6.87 | -4.214 | 0.3 | 101
8/7/2025 06:45 | -8 | 19 | 2.75 | 7.722 | 3.148 | 7.1 | 57 | 1.98 | 68.5 | 0.387 | 0.023 | 38.67 | 9402 | 8.15 | 58 |  | 179.74 | 3.35 | 6.87 | -4.214 | 0.3 | 101
8/7/2025 07:00 | 8 | 19 | 2.75 | 7.801 | 2.995 | 7.1 | 57 | 1.98 | 68.5 | 0.387 | 0.023 | 38.67 | 9402 | 8.13 | 58 |  | 180.45 | 3.33 | 6.87 | -4.214 | 0.47 | 101
8/7/2025 07:15 | 5 | 19 | 2.75 | 8.083 | 2.928 | 7.1 | 57 | 1.98 | 68.5 | 0.387 | 0.023 | 38.67 | 9402 | 8.11 | 58 |  | 180.62 | 3.22 | 6.86 | -4.214 | 0.29 | 101
8/7/2025 07:30 | 12 | 19 | 2.75 | 8.12 | 2.983 | 7.09 | 57 | 1.98 | 68.5 | 0.387 | 0.023 | 38.67 | 9402 | 8.1 | 58 |  | 180.51 | 3.2 | 6.86 | -4.214 | 0.27 | 93
8/7/2025 07:45 | 7 | 19 | 2.75 | 8.075 | 3.015 | 7.09 | 57 | 1.98 | 68.5 | 0.387 | 0.023 | 38.67 | 9402 | 8.09 | 58 |  | 180.39 | 3.22 | 6.85 | -4.214 | 0.29 | 101
8/7/2025 08:00 | 10 | 19 | 2.75 | 8.088 | 2.934 | 7.09 | 57 | 1.98 | 68.5 | 0.383 | 0.023 | 38.67 | 9402 | 8.08 | 58 |  | 180.11 | 3.21 | 6.86 | -4.214 | 0.28 | 101
8/7/2025 08:15 | 10 | 19 | 2.75 | 8.068 | 2.938 | 7.09 | 57 | 1.98 | 68.5 | 0.383 | 0.023 | 38.67 | 9402 | 8.08 | 58 |  | 179.76 | 3.21 | 6.86 | -4.214 | 0.29 | 101
8/7/2025 08:30 | 6 | 19 | 2.75 | 8.078 | 2.907 | 7.09 | 57 | 1.98 | 68.5 | 0.383 | 0.023 | 38.67 | 9402 | 8.07 | 58 |  | 180.35 | 3.21 | 6.85 | -4.214 | 0.3 | 101
8/7/2025 08:45 | 12 | 19 | 2.75 | 8.055 | 2.841 | 7.09 | 57 | 1.98 | 68.5 | 0.383 | 0.023 | 38.67 | 9402 | 8.07 | 58 |  | 180.39 | 3.22 | 6.85 | -4.214 | 0.3 | 93
8/7/2025 09:00 | 11 | 19 | 2.75 | 8.143 | 2.813 | 7.1 | 57 | 1.98 | 68.5 | 0.383 | 0.023 | 38.67 | 9402 | 8.07 | 58 |  | 180.52 | 3.19 | 6.85 | -4.214 | 0.31 | 101
8/7/2025 09:15 | 13 | 19 | 2.75 | 8.073 | 2.823 | 7.1 | 57 | 1.98 | 68.5 | 0.383 | 0.023 | 38.67 | 9402 | 8.07 | 58 |  | 180.1 | 3.21 | 6.85 | -4.214 | 0.29 | 91
8/7/2025 09:30 | 10 | 19 | 2.75 | 8.052 | 2.857 | 7.09 | 57 | 1.98 | 68.5 | 0.383 | 0.023 | 38.67 | 9402 | 8.07 | 58 |  | 180.09 | 3.22 | 6.85 | -4.214 | 0.29 | 101
8/7/2025 09:45 | 1 | 19 | 2.75 | 8.059 | 2.814 | 7.09 | 57 | 1.98 | 68.5 | 0.383 | 0.023 | 38.67 | 9402 | 8.07 | 58 |  | 179.63 | 3.21 | 6.84 | -4.214 | 0.29 | 101
8/7/2025 10:00 | 10 | 19 | 2.75 | 8.061 | 2.858 | 7.09 | 56 | 1.98 | 68.5 | 0.383 | 0.023 | 38.67 | 9402 | 8.08 | 58 |  | 180.25 | 3.22 | 6.84 | -4.214 | 0.28 | 101
8/7/2025 10:15 | 8 | 19 | 2.75 | 8.071 | 2.802 | 7.09 | 56 | 1.98 | 68.5 | 0.383 | 0.022 | 38.67 | 9402 | 8.09 | 58 |  | 180.37 | 3.22 | 6.85 | -4.214 | 0.28 | 101
8/7/2025 10:30 | 10 | 19 | 2.75 | 8.08 | 2.731 | 7.1 | 56 | 1.98 | 68.5 | 0.383 | 0.022 | 38.67 | 9402 | 8.1 | 58 |  | 180.47 | 3.22 | 6.86 | -4.214 | 0.29 | 101
8/7/2025 10:45 | 4 | 19 | 2.75 | 8.064 | 2.614 | 7.1 | 56 | 1.98 | 68.5 | 0.383 | 0.022 | 38.67 | 9402 | 8.11 | 58 |  | 180.4 | 3.22 | 6.8 | -4.214 | 0.3 | 101
8/7/2025 11:00 | 8 | 19 | 2.75 | 8.088 | 2.571 | 7.1 | 56 | 1.98 | 68.5 | 0.383 | 0.022 | 38.67 | 9402 | 8.12 | 58 |  | 179.79 | 3.2 | 6.78 | -4.214 | 0.26 | 101
8/7/2025 11:15 | 13 | 19 | 2.75 | 8.018 | 27.519 | 7.08 | 56 | 1.98 | 68.5 | 0.383 | 0.022 | 38.67 | 9402 | 8.11 | 58 |  | 180.44 | 3.24 | 6.8 | -4.214 | 0.27 | 92
8/7/2025 11:30 | 12 | 19 | 2.75 | 8.035 | 2.384 | 7.08 | 56 | 1.98 | 68.5 | 0.383 | 0.022 | 38.67 | 9402 | 8.11 | 58 |  | 180.94 | 3.24 | 6.85 | -4.214 | 0.28 | 93
8/7/2025 11:45 | 11 | 19 | 2.75 | 8.088 | 2.244 | 7.11 | 56 | 1.98 | 68.5 | 0.383 | 0.022 | 38.67 | 9402 | 8.11 | 58 |  | 180.64 | 3.22 | 6.87 | -4.214 | 0.3 | 101
8/7/2025 12:00 | 8 | 19 | 2.75 | 8.041 | 2.147 | 7.11 | 56 | 1.98 | 68.5 | 0.286 | 0.022 | 38.67 | 9402 | 8.11 | 58 |  | 181.3 | 3.25 | 6.87 | -3.49 | 0.33 | 101
8/7/2025 12:15 | 13 | 19 | 2.75 | 8.05 | 2.179 | 7.12 | 56 | 1.98 | 68.5 | 0.286 | 0.022 | 38.67 | 9402 | 8.11 | 58 |  | 164.52 | 2.94 | 6.87 | -3.49 | 0.31 | 92
8/7/2025 12:30 | 7 | 21 | 2.75 | 8.071 | 2.793 | 7.11 | 56 | 1.98 | 68.5 | 0.286 | 0.022 | 38.67 | 9402 | 8.1 | 58 |  | 177.84 | 3.17 | 6.83 | -3.49 | 0.33 | 101
8/7/2025 12:45 | 17 | 21 | 2.75 | 8.071 | 2.433 | 7.1 | 56 | 1.98 | 68.5 | 0.286 | 0.022 | 38.67 | 9402 | 8.09 | 58 |  | 178.33 | 3.18 | 6.82 | -3.49 | 0.34 | 90
8/7/2025 13:00 | 24 | 21 | 2.75 | 7.556 | 2.333 | 7.1 | 56 | 1.98 | 68.5 | 0.286 | 0.022 | 38.67 | 9402 | 8.09 | 58 |  | 177.7 | 3.39 | 6.81 | -3.49 | 0.32 | 83
8/7/2025 13:15 | 28 | 21 | 2.75 | 7.538 | 2.331 | 7.1 | 56 | 1.98 | 68.5 | 0.286 | 0.022 | 38.67 | 9402 | 8.09 | 58 |  | 178.17 | 3.4 | 6.81 | -3.49 | 0.3 | 80
8/7/2025 13:30 | 25 | 21 | 2.75 | 7.762 | 2.377 | 7.1 | 56 | 1.98 | 68.5 | 0.286 | 0.022 | 38.67 | 9402 | 8.09 | 58 |  | 177.96 | 3.3 | 6.81 | -3.49 | 0.31 | 84
8/7/2025 13:45 | 24 | 21 | 2.75 | 7.8 | 2.428 | 7.09 | 56 | 1.98 | 68.5 | 0.286 | 0.022 | 38.67 | 9402 | 8.09 | 58 |  | 178.11 | 3.29 | 6.8 | -3.49 | 0.31 | 84
8/7/2025 14:00 | 24 | 21 | 2.75 | 8.053 | 2.366 | 7.1 | 56 | 1.98 | 69 | 0.286 | 0.022 | 38.67 | 9402 | 8.09 | 59 |  | 178.14 | 3.19 | 6.8 | -3.49 | 0.3 | 84
8/7/2025 14:15 | 27 | 21 | 2.75 | 8.009 | 2.25 | 7.14 | 56 | 1.98 | 69 | 0.286 | 0.022 | 38.67 | 9402 | 8.09 | 59 |  | 177.8 | 3.2 | 6.81 | -3.49 | 0.31 | 82
8/7/2025 14:30 | 26 | 21 | 2.75 | 8.04 | 22.88 | 7.77 | 56 | 1.98 | 69 | 0.286 | 0.022 | 38.67 | 9402 | 8.09 | 59 |  | 177.98 | 3.19 | 6.8 | -3.49 | 0.29 | 82
8/7/2025 14:45 | 26 | 21 | 2.75 | 8.025 | 39.163 | 7.31 | 56 | 1.98 | 69 | 0.286 | 0.022 | 38.67 | 9402 | 8.09 | 59 |  | 177.72 | 3.19 | 6.79 | -3.49 | 0.32 | 81
8/7/2025 15:00 | 30 | 21 | 2.75 | 8.031 | 2.647 | 7.3 | 56 | 1.98 | 69 | 0.286 | 0.022 | 38.67 | 9402 | 8.09 | 59 |  | 177.61 | 3.18 | 6.81 | -3.49 | 0.28 | 80
8/7/2025 15:15 | 27 | 21 | 2.75 | 8.024 | 2.717 | 7.26 | 56 | 1.98 | 69 | 0.286 | 0.023 | 38.67 | 9402 | 8.09 | 59 |  | 178.15 | 3.2 | 6.8 | -3.49 | 0.29 | 83
8/7/2025 15:30 | 25 | 21 | 2.75 | 8.066 | 3.075 | 7.21 | 56 | 1.98 | 69 | 0.286 | 0.023 | 37.92 | 9301 | 8.1 | 59 |  | 176.98 | 3.16 | 6.78 | -3.49 | 0.31 | 82
8/7/2025 15:45 | 28 | 21 | 2.75 | 8.627 | 3.145 | 7.19 | 56 | 1.98 | 69 | 0.286 | 0.024 | 37.92 | 9301 | 8.11 | 59 |  | 177.47 | 2.96 | 6.77 | -3.49 | 0.3 | 80
8/7/2025 16:00 | 27 | 21 | 2.75 | 8.544 | 2.938 | 7.2 | 56 | 1.98 | 69 | 0.312 | 0.024 | 37.92 | 9301 | 8.11 | 59 |  | 177.76 | 3 | 6.78 | -3.49 | 0.31 | 80
8/7/2025 16:15 | 31 | 21 | 2.75 | 8.569 | 2.787 | 7.23 | 56 | 1.98 | 69 | 0.312 | 0.024 | 37.92 | 9301 | 8.11 | 59 |  | 177.95 | 2.99 | 6.8 | -3.49 | 0.3 | 77
8/7/2025 16:30 | 26 | 21 | 2.75 | 7.987 | 2.787 | 7.24 | 56 | 1.98 | 69 | 0.312 | 0.024 | 37.92 | 9301 | 8.09 | 59 |  | 177.77 | 3.21 | 6.83 | -3.49 | 0.29 | 82
8/7/2025 16:45 | 25 | 21 | 2.75 | 8.284 | 2.772 | 7.24 | 56 | 1.98 | 69 | 0.312 | 0.024 | 37.92 | 9301 | 8.08 | 59 |  | 178.15 | 3.1 | 6.79 | -3.49 | 0.32 | 80
8/7/2025 17:00 | 27 | 21 | 2.75 | 8.275 | 2.489 | 7.25 | 56 | 1.98 | 69 | 0.312 | 0.023 | 37.92 | 9301 | 8.1 | 59 |  | 177.68 | 3.09 | 6.78 | -3.49 | 0.29 | 79
8/7/2025 17:15 | 30 | 21 | 2.75 | 8.26 | 2.259 | 7.27 | 56 | 1.98 | 69 | 0.312 | 0.023 | 37.92 | 9301 | 8.14 | 59 |  | 178.07 | 3.1 | 6.67 | -3.49 | 0.29 | 76
8/7/2025 17:30 | 29 | 21 | 2.75 | 8.269 | 2.701 | 7.28 | 56 | 1.98 | 69 | 0.312 | 0.023 | 37.92 | 9301 | 8.16 | 59 |  | 177.59 | 3.09 | 6.8 | -3.49 | 0.25 | 79
8/7/2025 17:45 | 25 | 21 | 2.75 | 8.271 | 3.46 | 7.24 | 56 | 1.98 | 69 | 0.312 | 0.023 | 37.92 | 9301 | 8.16 | 59 |  | 177.68 | 3.09 | 6.74 | -3.49 | 0.29 | 82
8/7/2025 18:00 | 30 | 21 | 2.75 | 8.263 | 2.89 | 7.25 | 56 | 1.98 | 70.5 | 0.312 | 0.023 | 37.92 | 9301 | 8.16 | 59 |  | 177.49 | 3.09 | 6.87 | -3.49 | 0.29 | 77
8/7/2025 18:15 | 33 | 21 | 2.75 | 8.292 | 3.342 | 7.25 | 56 | 1.98 | 70.5 | 0.312 | 0.023 | 37.92 | 9301 | 8.15 | 59 |  | 177.68 | 3.09 | 6.9 | -3.49 | 0.29 | 76
8/7/2025 18:30 | 30 | 21 | 2.75 | 8.288 | 3.412 | 7.24 | 56 | 1.98 | 70.5 | 0.312 | 0.023 | 37.92 | 9301 | 8.14 | 59 |  | 178.13 | 3.09 | 6.93 | -3.49 | 0.28 | 77
8/7/2025 18:45 | 13 | 21 | 2.75 | 8.273 | 3.239 | 7.26 | 56 | 1.98 | 70.5 | 0.312 | 0.023 | 37.92 | 9301 | 8.13 | 59 |  | 0 | 0 | 7 | -3.49 | 0.28 | 88
8/7/2025 19:00 | 27 | 21 | 2.75 | 8.242 | 3.708 | 7.31 | 56 | 1.98 | 70.5 | 0.312 | 0.023 | 37.92 | 9301 | 8.12 | 59 |  | 0 | 0 | 7.09 | -3.49 | 0.3 | 77
8/7/2025 19:15 | 26 | 21 | 2.75 | 8.272 | 3.842 | 7.32 | 56 | 1.98 | 70.5 | 0.312 | 0.023 | 37.92 | 9301 | 8.11 | 59 |  | 0 | 0 | 7.07 | -3.49 | 0.29 | 81
8/7/2025 19:30 | 26 | 21 | 2.75 | 8.296 | 3.673 | 7.32 | 56 | 1.98 | 70.5 | 0.312 | 0.023 | 37.92 | 9301 | 8.1 | 59 |  | 0 | 0 | 7.05 | -3.49 | 0.28 | 79
8/7/2025 19:45 | 25 | 21 | 2.75 | 8.228 | 3.459 | 7.33 | 56 | 1.98 | 70.5 | 0.312 | 0.022 | 37.92 | 9301 | 8.08 | 59 |  | 0 | 0 | 7.05 | -3.49 | 0.28 | 80
8/7/2025 20:00 | 25 | 21 | 2.75 | 7.501 | 3.799 | 7.33 | 56 | 1.98 | 70.5 | 0.392 | 0.022 | 37.92 | 9301 | 8.07 | 59 |  | 0 | 0 | 7.05 | -3.49 | 0.1 | 80
8/7/2025 20:15 | 26 | 21 | 2.75 | 7.495 | 4.032 | 7.31 | 56 | 1.98 | 70.5 | 0.392 | 0.022 | 37.92 | 9301 | 8.06 | 59 |  | 0 | 0 | 7.05 | -3.49 | 0.25 | 80
8/7/2025 20:30 | 19 | 21 | 2.75 | 7.815 | 4.346 | 7.29 | 56 | 1.98 | 70.5 | 0.392 | 0.022 | 37.92 | 9301 | 8.05 | 59 |  | 0 | 0 | 7.05 | -3.49 | 0.25 | 85
8/7/2025 20:45 | 22 | 21 | 2.75 | 7.831 | 5.28 | 7.26 | 56 | 1.98 | 70.5 | 0.392 | 0.022 | 37.92 | 9301 | 8.04 | 59 |  | 0 | 0 | 7.05 | -3.49 | 0.27 | 83
8/7/2025 21:00 | 22 | 21 | 2.75 | 7.872 | 4.818 | 7.27 | 56 | 1.98 | 70.5 | 0.392 | 0.022 | 37.92 | 9301 | 8.03 | 59 |  | 0 | 0 | 7.05 | -3.49 | 0.29 | 82
8/7/2025 21:15 | 22 | 21 | 2.75 | 7.84 | 4.701 | 7.28 | 56 | 1.98 | 70.5 | 0.392 | 0.022 | 37.92 | 9301 | 8.02 | 59 |  | 0 | 0 | 7.05 | -3.49 | 0.29 | 84
8/7/2025 21:30 | 23 | 21 | 2.75 | 7.799 | 4.676 | 7.28 | 56 | 1.98 | 70.5 | 0.392 | 0.022 | 37.92 | 9301 | 8.02 | 59 |  | 0 | 0 | 7.05 | -3.49 | 0.3 | 81
8/7/2025 21:45 | 17 | 21 | 2.75 | 7.842 | 4.794 | 7.29 | 56 | 1.98 | 70.5 | 0.392 | 0.022 | 37.92 | 9301 | 8.02 | 59 |  | 0 | 0 | 7.05 | -3.49 | 0.28 | 88
8/7/2025 22:00 | 21 | 21 | 2.75 | 7.824 | 4.377 | 7.3 | 57 | 1.98 | 69 | 0.392 | 0.022 | 37.92 | 9301 | 8.02 | 59 |  | 0 | 0 | 7.06 | -3.49 | 0.29 | 86
8/7/2025 22:15 | 21 | 21 | 2.75 | 7.824 | 4.264 | 7.32 | 57 | 1.98 | 69 | 0.392 | 0.022 | 37.92 | 9301 | 8.02 | 59 |  | 0 | 0 | 7.06 | -3.49 | 0.29 | 84
8/7/2025 22:30 | 17 | 21 | 2.75 | 7.703 | 4.314 | 7.31 | 57 | 1.98 | 69 | 0.392 | 0.022 | 37.92 | 9301 | 8.02 | 59 |  | 0 | 0 | 7.06 | -3.49 | 0.28 | 89
8/7/2025 22:45 | 18 | 21 | 2.75 | 7.306 | 4.169 | 7.31 | 57 | 1.98 | 69 | 0.392 | 0.022 | 37.92 | 9301 | 8.02 | 59 |  | 0 | 0 | 7.07 | -3.49 | 0.28 | 88
8/7/2025 23:00 | 18 | 21 | 2.75 | 7.637 | 5.141 | 7.28 | 57 | 1.98 | 69 | 0.392 | 0.022 | 37.92 | 9301 | 8.02 | 59 |  | 0 | 0 | 7.07 | -3.49 | 0.28 | 89
8/7/2025 23:15 | 13 | 21 | 2.75 | 7.626 | 5.02 | 7.27 | 57 | 1.98 | 69 | 0.392 | 0.022 | 37.92 | 9301 | 8.02 | 59 |  | 0 | 0 | 7.07 | -3.49 | 0.29 | 92
8/7/2025 23:30 | 9 | 21 | 2.75 | 7.63 | 5.528 | 7.25 | 57 | 1.98 | 69 | 0.392 | 0.021 | 37.92 | 9301 | 8.02 | 59 |  | 0 | 0 | 7.07 | -3.49 | 0.27 | 101
8/7/2025 23:45 | 17 | 21 | 2.75 | 7.602 | 5.744 | 7.24 | 57 | 1.98 | 69 | 0.392 | 0.021 | 37.92 | 9301 | 8.02 | 59 |  | 0 | 0 | 7.07 | -3.49 | 0.27 | 89
8/8/2025 00:00 | 16 | 21 | 2.75 | 7.593 | 5.273 | 7.25 | 57 | 1.98 | 69 | 0.291 | 0.022 | 37.92 | 9301 | 8.02 | 59 |  | 0 | 0 | 7.08 | -3.49 | 0.27 | 90
8/8/2025 00:15 | 17 | 21 | 2.75 | 7.644 | 5.445 | 7.25 | 57 | 1.98 | 69 | 0.291 | 0.022 | 37.92 | 9301 | 8.03 | 59 |  | 0 | 0 | 7.08 | -3.49 | 0.25 | 88
8/8/2025 00:30 | 11 | 21 | 2.75 | 7.611 | 5.18 | 7.26 | 57 | 1.98 | 69 | 0.291 | 0.022 | 37.92 | 9301 | 8.05 | 59 |  | 0 | 0 | 7.08 | -3.49 | 0.28 | 93
8/8/2025 00:45 | 17 | 21 | 2.75 | 7.625 | 4.895 | 7.26 | 57 | 1.98 | 69 | 0.291 | 0.022 | 37.92 | 9301 | 8.08 | 59 |  | 0 | 0 | 7.08 | -3.49 | 0.28 | 88
8/8/2025 01:00 | 22 | 21 | 2.75 | 7.616 | 4.658 | 7.27 | 57 | 1.98 | 69 | 0.291 | 0.022 | 37.92 | 9301 | 8.09 | 59 |  | 0 | 0 | 7.09 | -3.49 | 0.29 | 83
8/8/2025 01:15 | 22 | 21 | 2.75 | 7.599 | 4.832 | 7.26 | 57 | 1.98 | 69 | 0.291 | 0.022 | 37.92 | 9301 | 8.1 | 59 |  | 0 | 0 | 7.09 | -3.49 | 0.29 | 82
8/8/2025 01:30 | 19 | 21 | 2.75 | 7.613 | 5.512 | 7.25 | 57 | 1.98 | 69 | 0.291 | 0.022 | 37.92 | 9301 | 8.11 | 59 |  | 181.17 | 3.43 | 7.09 | -3.49 | 0.28 | 86
8/8/2025 01:45 | 21 | 21 | 2.75 | 7.604 | 4.544 | 7.2 | 57 | 1.98 | 69 | 0.291 | 0.022 | 37.92 | 9301 | 8.11 | 59 |  | 180.96 | 3.43 | 7.09 | -3.49 | 0.27 | 84
8/8/2025 02:00 | 23 | 21 | 2.75 | 7.877 | 4.532 | 7.19 | 57 | 1.98 | 68.9 | 0.291 | 0.022 | 37.92 | 9301 | 8.12 | 58 |  | 180.77 | 3.3 | 7.09 | -3.49 | 0.29 | 82
8/8/2025 02:15 | 23 | 21 | 2.75 | 7.871 | 4.469 | 7.19 | 57 | 1.98 | 68.9 | 0.291 | 0.022 | 37.92 | 9301 | 8.12 | 58 |  | 180.79 | 3.31 | 7.09 | -3.49 | 0.27 | 81
8/8/2025 02:30 | 23 | 21 | 2.75 | 7.89 | 4.303 | 7.19 | 57 | 1.98 | 68.9 | 0.291 | 0.022 | 37.92 | 9301 | 8.12 | 58 |  | 180.59 | 3.3 | 7.1 | -3.49 | 0.27 | 79
8/8/2025 02:45 | 20 | 21 | 2.75 | 7.84 | 4.204 | 7.2 | 57 | 1.98 | 68.9 | 0.291 | 0.022 | 37.92 | 9301 | 8.12 | 58 |  | 180.97 | 3.32 | 7.1 | -3.49 | 0.27 | 83
8/8/2025 03:00 | 25 | 21 | 2.75 | 7.861 | 4.181 | 7.2 | 57 | 1.98 | 68.9 | 0.291 | 0.022 | 37.92 | 9301 | 8.11 | 58 |  | 180.71 | 3.31 | 7.1 | -3.49 | 0.27 | 77
8/8/2025 03:15 | 22 | 21 | 2.75 | 7.843 | 3.97 | 7.2 | 57 | 1.98 | 68.9 | 0.291 | 0.022 | 37.92 | 9301 | 8.11 | 58 |  | 180.28 | 3.31 | 7.1 | -3.49 | 0.27 | 81
8/8/2025 03:30 | 23 | 21 | 2.75 | 7.885 | 3.956 | 7.21 | 57 | 1.98 | 68.9 | 0.291 | 0.022 | 37.92 | 9301 | 8.1 | 58 |  | 180.92 | 3.3 | 7.1 | -3.49 | 0.29 | 81
8/8/2025 03:45 | 21 | 21 | 2.75 | 7.832 | 3.942 | 7.21 | 57 | 1.98 | 68.9 | 0.291 | 0.022 | 37.92 | 9301 | 8.11 | 58 |  | 180.63 | 3.32 | 7.1 | -3.49 | 0.27 | 83
8/8/2025 04:00 | 20 | 21 | 2.75 | 7.902 | 3.941 | 7.2 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.11 | 58 |  | 180.52 | 3.29 | 7.1 | -3.49 | 0.32 | 82
8/8/2025 04:15 | 24 | 21 | 2.75 | 7.864 | 3.841 | 7.21 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.11 | 58 |  | 180.78 | 3.31 | 7.1 | -3.49 | 0.27 | 79
8/8/2025 04:30 | 26 | 21 | 2.75 | 7.821 | 3.647 | 7.21 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.11 | 58 |  | 180.2 | 3.32 | 7.1 | -3.49 | 0.28 | 76
8/8/2025 04:45 | 16 | 21 | 2.75 | 7.832 | 3.703 | 7.21 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.11 | 58 |  | 179.9 | 3.31 | 7.1 | -3.49 | 0.47 | 88
8/8/2025 05:00 | 15 | 21 | 2.75 | 7.846 | 3.69 | 7.21 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.11 | 58 |  | 180.63 | 3.32 | 7.09 | -3.49 | 0.27 | 89
8/8/2025 05:15 | 28 | 21 | 2.75 | 7.862 | 3.653 | 7.2 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.11 | 58 |  | 180.28 | 3.3 | 7.09 | -3.49 | 0.27 | 75
8/8/2025 05:30 | 23 | 21 | 2.75 | 7.857 | 3.945 | 7.2 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.1 | 58 |  | 180.59 | 3.31 | 7.09 | -3.49 | 0.27 | 78
8/8/2025 05:45 | 26 | 21 | 2.75 | 7.807 | 4.182 | 7.19 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.1 | 58 |  | 180.25 | 3.32 | 7.09 | -3.49 | 0.26 | 76
8/8/2025 06:00 | 21 | 21 | 2.75 | 7.781 | 4.021 | 7.2 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.1 | 58 |  | 180.34 | 3.34 | 7.1 | -3.49 | 0.27 | 83
8/8/2025 06:15 | 26 | 21 | 2.75 | 7.408 | 3.806 | 7.21 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.1 | 58 |  | 179.45 | 3.49 | 7.1 | -3.49 | 0.28 | 75
8/8/2025 06:30 | 21 | 21 | 2.75 | 7.918 | 4.46 | 7.23 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.09 | 58 |  | 0 | 0 | 7.1 | -3.49 | 0.27 | 82
8/8/2025 06:45 | 13 | 21 | 2.75 | 7.876 | 4.604 | 7.24 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.09 | 58 |  | 0 | 0 | 7.13 | -3.49 | 0.28 | 90
8/8/2025 07:00 | 13 | 21 | 2.75 | 7.911 | 4.632 | 7.25 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.08 | 58 |  | 0 | 0 | 7.12 | -3.49 | 0.27 | 91
8/8/2025 07:15 | 15 | 21 | 2.75 | 7.882 | 4.603 | 7.22 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.08 | 58 |  | 176.97 | 3.23 | 7.11 | -3.49 | 0.27 | 91
8/8/2025 07:30 | 17 | 21 | 2.75 | 7.876 | 13.48 | 7.18 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.07 | 58 |  | 177.28 | 3.24 | 7.09 | -3.49 | 0.3 | 86
8/8/2025 07:45 | 20 | 21 | 2.75 | 7.731 | 7.296 | 7.16 | 57 | 1.98 | 68.9 | 0.36 | 0.021 | 37.92 | 9301 | 8.07 | 58 |  | 177.77 | 3.31 | 7.11 | -3.49 | 0.25 | 85
8/8/2025 08:00 | 22 | 21 | 2.75 | 7.276 | 5.777 | 7.16 | 57 | 1.98 | 68.9 | 0.361 | 0.021 | 37.92 | 9301 | 8.07 | 58 |  | 177 | 3.5 | 7.11 | -3.49 | 0.32 | 81
8/8/2025 08:15 | 17 | 21 | 2.75 | 7.665 | 5.173 | 7.16 | 57 | 1.98 | 68.9 | 0.361 | 0.021 | 37.92 | 9301 | 8.07 | 58 |  | 177.43 | 3.33 | 7.09 | -3.49 | 0.28 | 87
8/8/2025 08:30 | 13 | 21 | 2.75 | 7.65 | 2.681 | 7.08 | 57 | 1.98 | 68.9 | 0.361 | 0.021 | 37.92 | 9301 | 8.09 | 58 |  | 176.99 | 3.33 | 7.07 | -3.49 | 0.28 | 91
8/8/2025 08:45 | 26 | 21 | 2.75 | 7.646 | 2.508 | 7.08 | 57 | 1.98 | 68.9 | 0.361 | 0.021 | 37.92 | 9301 | 8.1 | 58 |  | 176.84 | 3.33 | 7.08 | -3.49 | 0.27 | 73
8/8/2025 09:00 | 27 | 21 | 2.75 | 8.06 | 2.496 | 7.11 | 57 | 1.98 | 68.9 | 0.361 | 0.021 | 37.92 | 9301 | 8.11 | 58 |  | 176.59 | 3.15 | 7.08 | -3.49 | 0.26 | 76
8/8/2025 09:15 | 28 | 21 | 2.75 | 8.072 | 2.684 | 7.13 | 57 | 1.98 | 68.9 | 0.361 | 0.021 | 37.92 | 9301 | 8.12 | 58 |  | 177.03 | 3.16 | 6.81 | -3.49 | 0.29 | 73
8/8/2025 09:30 | 24 | 21 | 2.75 | 8.069 | 2.81 | 7.13 | 57 | 1.98 | 68.9 | 0.361 | 0.021 | 37.92 | 9301 | 8.12 | 58 |  | 176.84 | 3.16 | 6.73 | -3.49 | 0.26 | 79
8/8/2025 09:45 | 28 | 21 | 2.75 | 7.075 | 2.874 | 7.13 | 57 | 1.98 | 68.9 | 0.361 | 0.021 | 37.92 | 9301 | 8.11 | 58 |  | 171.82 | 3.5 | 6.73 | -3.49 | 0.35 | 72
8/8/2025 10:00 | 15 | 21 | 2.75 | 7.131 | 2.99 | 7.13 | 55 | 1.98 | 68.9 | 0.361 | 0.021 | 37.92 | 9301 | 8.12 | 58 |  | 173.01 | 3.49 | 6.74 | -3.49 | 0.28 | 91
8/8/2025 10:15 | 13 | 19 | 2.75 | 7.351 | 2.946 | 7.14 | 55 | 1.98 | 68.9 | 0.361 | 0.021 | 37.92 | 9301 | 8.12 | 58 |  | 176.7 | 3.46 | 6.78 | -3.49 | 0.26 | 98
8/8/2025 10:30 | 9 | 19 | 2.75 | 7.357 | 3.115 | 7.13 | 55 | 1.98 | 68.9 | 0.361 | 0.021 | 37.92 | 9301 | 8.12 | 58 |  | 177.26 | 3.47 | 6.8 | -3.49 | 0.22 | 101
8/8/2025 10:45 | 9 | 19 | 2.75 | 8.538 | 3.038 | 7.14 | 55 | 1.98 | 68.9 | 0.361 | 0.021 | 37.92 | 9301 | 8.11 | 58 |  | 176.88 | 2.98 | 6.83 | -3.49 | 0.27 | 101
8/8/2025 11:00 | 11 | 19 | 2.75 | 7.149 | 3.074 | 7.15 | 55 | 1.98 | 68.9 | 0.361 | 0.021 | 37.31 | 9118 | 8.11 | 58 |  | 173.67 | 3.5 | 6.85 | -3.49 | 0.29 | 99
8/8/2025 11:15 | 10 | 19 | 2.75 | 7.414 | 2.947 | 7.14 | 55 | 1.98 | 68.9 | 0.361 | 0.022 | 37.31 | 9118 | 8.11 | 58 |  | 176.51 | 3.43 | 6.89 | -3.49 | 0.24 | 101
8/8/2025 11:30 | 7 | 19 | 2.75 | 7.382 | 3.073 | 7.14 | 55 | 1.98 | 68.9 | 0.361 | 0.022 | 37.31 | 9118 | 8.11 | 58 |  | 176.67 | 3.45 | 6.87 | -3.49 | 0.29 | 101
8/8/2025 11:45 | 10 | 19 | 2.75 | 7.469 | 3.016 | 7.14 | 55 | 1.98 | 68.9 | 0.361 | 0.022 | 37.31 | 9118 | 8.11 | 58 |  | 176.75 | 3.41 | 6.87 | -3.49 | 0.26 | 101
8/8/2025 12:00 | 9 | 19 | 2.75 | 7.425 | 2.85 | 7.14 | 55 | 1.98 | 68.9 | 0.266 | 0.022 | 37.31 | 9118 | 8.1 | 58 |  | 176.84 | 3.43 | 6.89 | -3.109 | 0.26 | 101
8/8/2025 12:15 | 10 | 19 | 2.75 | 7.636 | 2.782 | 7.15 | 55 | 1.98 | 68.9 | 0.266 | 0.022 | 37.31 | 9118 | 8.07 | 58 |  | 177.15 | 3.34 | 6.9 | -3.109 | 0.27 | 101
8/8/2025 12:30 | 10 | 19 | 2.75 | 7.885 | 3.117 | 7.21 | 55 | 1.98 | 68.9 | 0.266 | 0.022 | 36.95 | 8934 | 8.09 | 58 |  | 0 | 0 | 6.89 | -3.109 | 0.28 | 101
8/8/2025 12:45 | 8 | 19 | 2.75 | 7.865 | 3.226 | 7.23 | 55 | 1.98 | 68.9 | 0.266 | 0.023 | 36.95 | 8934 | 8.15 | 58 |  | 0 | 0 | 6.89 | -3.109 | 0.3 | 101
8/8/2025 13:00 | 7 | 19 | 2.75 | 7.846 | 3.444 | 7.24 | 55 | 1.98 | 68.9 | 0.266 | 0.023 | 36.95 | 8934 | 8.17 | 58 |  | 0 | 0 | 6.9 | -3.109 | 0.29 | 101
8/8/2025 13:15 | 6 | 19 | 2.75 | 7.362 | 4.437 | 7.2 | 55 | 1.98 | 68.9 | 0.266 | 0.023 | 36.95 | 8934 | 8.17 | 58 |  | 0 | 0 | 6.87 | -3.109 | 0.27 | 101
8/8/2025 13:30 | 7 | 19 | 2.75 | 7.522 | 3.712 | 7.15 | 55 | 1.98 | 68.9 | 0.266 | 0.023 | 36.95 | 8934 | 8.16 | 58 |  | 181.1 | 3.47 | 6.87 | -3.109 | 0.3 | 101
8/8/2025 13:45 | 10 | 19 | 2.75 | 7.741 | 4.109 | 7.16 | 55 | 1.98 | 68.9 | 0.266 | 0.023 | 36.95 | 8934 | 8.14 | 58 |  | 180.96 | 3.37 | 6.89 | -3.109 | 0.29 | 101
8/8/2025 14:00 | 8 | 19 | 2.75 | 7.752 | 3.683 | 7.17 | 55 | 1.98 | 68.9 | 0.266 | 0.023 | 36.95 | 8934 | 8.15 | 59 |  | 181.52 | 3.37 | 6.89 | -3.109 | 0.27 | 101
8/8/2025 14:15 | 9 | 19 | 2.75 | 7.745 | 3.366 | 7.18 | 55 | 1.98 | 68.9 | 0.266 | 0.023 | 36.95 | 8934 | 8.19 | 59 |  | 181.36 | 3.37 | 6.91 | -3.109 | 0.28 | 101
8/8/2025 14:30 | 5 | 19 | 2.75 | 7.737 | 3.437 | 7.18 | 55 | 1.98 | 68.9 | 0.266 | 0.024 | 36.95 | 8934 | 8.23 | 59 |  | 180.81 | 3.37 | 6.9 | -3.109 | 0.27 | 101
8/8/2025 14:45 | 8 | 19 | 2.75 | 7.715 | 3.453 | 7.16 | 55 | 1.98 | 68.9 | 0.266 | 0.024 | 36.95 | 8934 | 8.24 | 59 |  | 180.38 | 3.37 | 6.88 | -3.109 | 0.27 | 101
8/8/2025 15:00 | 11 | 19 | 2.75 | 7.129 | 4.195 | 7.14 | 55 | 1.98 | 68.9 | 0.266 | 0.023 | 36.95 | 8934 | 8.23 | 59 |  | 172.98 | 3.49 | 6.87 | -3.109 | 0.27 | 101
8/8/2025 15:15 | 13 | 19 | 2.75 | 7.18 | 4.258 | 7.12 | 55 | 1.98 | 68.9 | 0.266 | 0.023 | 36.95 | 8934 | 8.22 | 59 |  | 174.48 | 3.5 | 6.86 | -3.109 | 0.24 | 101
8/8/2025 15:30 | 14 | 19 | 2.75 | 7.648 | 4.028 | 7.12 | 55 | 1.98 | 68.9 | 0.266 | 0.023 | 36.95 | 8934 | 8.22 | 59 |  | 180.89 | 3.41 | 6.84 | -3.109 | 0.25 | 100
8/8/2025 15:45 | 13 | 19 | 2.75 | 7.681 | 3.699 | 7.13 | 55 | 1.98 | 68.9 | 0.266 | 0.023 | 36.95 | 8934 | 8.21 | 59 |  | 181.05 | 3.39 | 6.85 | -3.109 | 0.27 | 100
8/8/2025 16:00 | 15 | 19 | 2.75 | 7.683 | 3.584 | 7.14 | 55 | 1.98 | 68.9 | 0.211 | 0.023 | 36.95 | 8934 | 8.21 | 59 |  | 181.1 | 3.39 | 6.86 | -3.109 | 0.27 | 100
8/8/2025 16:15 | 15 | 19 | 2.75 | 7.626 | 3.388 | 7.14 | 55 | 1.98 | 68.9 | 0.211 | 0.023 | 36.95 | 8934 | 8.21 | 59 |  | 181.05 | 3.42 | 6.86 | -3.109 | 0.32 | 100
8/8/2025 16:30 | 15 | 19 | 2.75 | 7.669 | 3.317 | 7.13 | 55 | 1.98 | 68.9 | 0.211 | 0.023 | 36.95 | 8934 | 8.21 | 59 |  | 181.54 | 3.41 | 6.86 | -3.109 | 0.28 | 100
8/8/2025 16:45 | 15 | 19 | 2.75 | 7.66 | 3.264 | 7.14 | 55 | 1.98 | 68.9 | 0.211 | 0.023 | 36.95 | 8934 | 8.21 | 59 |  | 181.02 | 3.4 | 6.86 | -3.109 | 0.27 | 100
8/8/2025 17:00 | 15 | 19 | 2.75 | 7.634 | 3.08 | 7.14 | 55 | 1.98 | 68.9 | 0.211 | 0.024 | 36.95 | 8934 | 8.21 | 59 |  | 181.03 | 3.41 | 6.87 | -3.109 | 0.28 | 100
8/8/2025 17:15 | 15 | 19 | 2.75 | 7.623 | 2.92 | 7.16 | 55 | 1.98 | 68.9 | 0.211 | 0.024 | 36.95 | 8934 | 8.21 | 59 |  | 181.22 | 3.42 | 6.88 | -3.109 | 0.28 | 100
8/8/2025 17:30 | 14 | 19 | 2.75 | 7.639 | 2.658 | 7.18 | 55 | 1.98 | 68.9 | 0.211 | 0.024 | 40.95 | 9888 | 8.22 | 59 |  | 64.95 | 1.22 | 6.9 | -3.109 | 0.26 | 100
8/8/2025 17:45 | 13 | 19 | 2.75 | 7.684 | 39.935 | 7.16 | 55 | 1.98 | 68.9 | 0.211 | 0.025 | 40.95 | 9888 | 8.22 | 59 |  | 177.47 | 3.33 | 6.9 | -3.109 | 0.3 | 100
8/8/2025 18:00 | 11 | 19 | 2.75 | 7.624 | 5.705 | 7.21 | 55 | 1.98 | 69 | 0.211 | 0.025 | 40.95 | 9888 | 8.22 | 59 |  | 0 | 0 | 6.89 | -3.109 | 0.29 | 101
8/8/2025 18:15 | 12 | 19 | 2.75 | 7.636 | 4.187 | 7.24 | 55 | 1.98 | 69 | 0.211 | 0.025 | 40.95 | 9888 | 8.22 | 59 |  | 177.65 | 3.35 | 6.89 | -3.109 | 0.24 | 101
8/8/2025 18:30 | 13 | 19 | 2.75 | 7.603 | 12.226 | 7.18 | 55 | 1.98 | 69 | 0.211 | 0.025 | 40.95 | 9888 | 8.21 | 59 |  | 177.58 | 3.36 | 6.9 | -3.109 | 0.29 | 101
8/8/2025 18:45 | 13 | 19 | 2.75 | 7.581 | 5.684 | 7.17 | 55 | 1.98 | 69 | 0.211 | 0.025 | 40.95 | 9888 | 8.2 | 59 |  | 177.69 | 3.38 | 6.87 | -3.109 | 0.3 | 100
8/8/2025 19:00 | 14 | 19 | 2.75 | 7.308 | 4.248 | 7.16 | 55 | 1.98 | 69 | 0.211 | 0.025 | 40.95 | 9888 | 8.21 | 59 |  | 177.87 | 3.5 | 6.87 | -3.109 | 0.28 | 100
8/8/2025 19:15 | 15 | 19 | 2.75 | 7.518 | 3.688 | 7.16 | 55 | 1.98 | 69 | 0.211 | 0.025 | 40.95 | 9888 | 8.25 | 59 |  | 177.29 | 3.4 | 6.87 | -3.109 | 0.28 | 100
8/8/2025 19:30 | 14 | 19 | 2.75 | 7.753 | 3.283 | 7.17 | 55 | 1.98 | 69 | 0.211 | 0.025 | 40.95 | 9888 | 8.29 | 59 |  | 177.37 | 3.29 | 6.87 | -3.109 | 0.29 | 100
8/8/2025 19:45 | 14 | 19 | 2.75 | 7.75 | 3.274 | 7.18 | 55 | 1.98 | 69 | 0.211 | 0.025 | 40.95 | 9888 | 8.31 | 59 |  | 177.09 | 3.29 | 6.88 | -3.109 | 0.26 | 100
8/8/2025 20:00 | 14 | 19 | 2.75 | 7.732 | 3.066 | 7.17 | 55 | 1.98 | 69 | 0.206 | 0.025 | 40.95 | 9888 | 8.32 | 59 |  | 177.58 | 3.31 | 6.87 | -3.109 | 0.29 | 100
8/8/2025 20:15 | 14 | 19 | 2.75 | 7.319 | 3.058 | 7.16 | 55 | 1.98 | 69 | 0.206 | 0.024 | 40.95 | 9888 | 8.33 | 59 |  | 177.34 | 3.49 | 6.87 | -3.109 | 0.27 | 100
8/8/2025 20:30 | 14 | 19 | 2.75 | 7.341 | 3.28 | 7.15 | 55 | 1.98 | 69 | 0.206 | 0.025 | 40.95 | 9888 | 8.32 | 59 |  | 177.56 | 3.48 | 6.88 | -3.109 | 0.26 | 100
8/8/2025 20:45 | 13 | 19 | 2.75 | 7.538 | 3.63 | 7.13 | 55 | 1.98 | 69 | 0.206 | 0.024 | 40.95 | 9888 | 8.31 | 59 |  | 177.59 | 3.39 | 6.85 | -3.109 | 0.27 | 101
8/8/2025 21:00 | 14 | 19 | 2.75 | 7.562 | 3.257 | 7.13 | 55 | 1.98 | 69 | 0.206 | 0.024 | 40.95 | 9888 | 8.31 | 59 |  | 177.36 | 3.38 | 6.85 | -3.109 | 0.25 | 100
8/8/2025 21:15 | 12 | 19 | 2.75 | 7.562 | 3.203 | 7.14 | 55 | 1.98 | 69 | 0.206 | 0.025 | 40.95 | 9888 | 8.31 | 59 |  | 177.56 | 3.38 | 6.84 | -3.109 | 0.27 | 101
8/8/2025 21:30 | 13 | 19 | 2.75 | 7.783 | 3.129 | 7.14 | 55 | 1.98 | 69 | 0.206 | 0.024 | 40.95 | 9888 | 8.3 | 59 |  | 177.62 | 3.29 | 6.86 | -3.109 | 0.28 | 101
8/8/2025 21:45 | 13 | 19 | 2.75 | 7.765 | 3.315 | 7.14 | 55 | 1.98 | 69 | 0.206 | 0.024 | 40.71 | 9754 | 8.3 | 59 |  | 176.9 | 3.28 | 6.85 | -3.109 | 0.27 | 101
8/8/2025 22:00 | 13 | 19 | 2.75 | 7.778 | 3.46 | 7.14 | 57 | 1.98 | 68.9 | 0.206 | 0.025 | 40.71 | 9754 | 8.3 | 59 |  | 177.04 | 3.28 | 6.86 | -3.109 | 0.27 | 100
8/8/2025 22:15 | 11 | 19 | 2.75 | 7.758 | 3.36 | 7.14 | 57 | 1.98 | 68.9 | 0.206 | 0.025 | 40.71 | 9754 | 8.3 | 59 |  | 176.94 | 3.28 | 6.84 | -3.109 | 0.29 | 101
8/8/2025 22:30 | 12 | 19 | 2.75 | 7.784 | 3.344 | 7.14 | 57 | 1.98 | 68.9 | 0.206 | 0.025 | 40.71 | 9754 | 8.3 | 59 |  | 177.53 | 3.28 | 6.83 | -3.109 | 0.28 | 101
8/8/2025 22:45 | 13 | 19 | 2.75 | 7.754 | 3.301 | 7.14 | 57 | 1.98 | 68.9 | 0.206 | 0.025 | 40.71 | 9754 | 8.3 | 59 |  | 177.09 | 3.29 | 6.85 | -3.109 | 0.27 | 101
8/8/2025 23:00 | 12 | 19 | 2.75 | 7.394 | 3.169 | 7.14 | 57 | 1.98 | 68.9 | 0.206 | 0.025 | 40.71 | 9754 | 8.3 | 59 |  | 177.64 | 3.46 | 6.86 | -3.109 | 0.28 | 101
8/8/2025 23:15 | 13 | 19 | 2.75 | 7.414 | 3.331 | 7.14 | 57 | 1.98 | 68.9 | 0.206 | 0.025 | 40.71 | 9754 | 8.31 | 59 |  | 176.94 | 3.44 | 6.87 | -3.109 | 0.27 | 100
8/8/2025 23:30 | 12 | 19 | 2.75 | 7.681 | 4.358 | 7.14 | 57 | 1.98 | 68.9 | 0.206 | 0.025 | 40.71 | 9754 | 8.34 | 59 |  | 0 | 0 | 6.84 | -3.109 | 0.28 | 101
8/8/2025 23:45 | 10 | 19 | 2.75 | 7.728 | 3.938 | 7.13 | 57 | 1.98 | 68.9 | 0.206 | 0.024 | 40.71 | 9754 | 8.37 | 59 |  | 181.04 | 3.37 | 6.82 | -3.109 | 0.27 | 101
8/9/2025 00:00 | 11 | 19 | 2.75 | 7.801 | 4.418 | 7.12 | 57 | 1.98 | 68.9 | 0.296 | 0.024 | 40.71 | 9754 | 8.38 | 59 |  | 181.23 | 3.35 | 6.82 | -3.109 | 0.28 | 101
8/9/2025 00:15 | 10 | 19 | 2.75 | 7.726 | 3.996 | 7.12 | 57 | 1.98 | 68.9 | 0.296 | 0.024 | 40.71 | 9754 | 8.37 | 59 |  | 180.98 | 3.37 | 6.83 | -3.109 | 0.31 | 101
8/9/2025 00:30 | 11 | 19 | 2.75 | 7.717 | 3.49 | 7.13 | 57 | 1.98 | 68.9 | 0.296 | 0.024 | 40.71 | 9754 | 8.36 | 59 |  | 181.12 | 3.38 | 6.84 | -3.109 | 0.28 | 101
8/9/2025 00:45 | 12 | 19 | 2.75 | 7.714 | 3.464 | 7.13 | 57 | 1.98 | 68.9 | 0.296 | 0.024 | 40.71 | 9754 | 8.35 | 59 |  | 180.91 | 3.38 | 6.86 | -3.109 | 0.29 | 101
8/9/2025 01:00 | 12 | 19 | 2.75 | 7.724 | 3.348 | 7.13 | 57 | 1.98 | 68.9 | 0.296 | 0.024 | 40.71 | 9754 | 8.35 | 59 |  | 181.13 | 3.38 | 6.87 | -3.109 | 0.36 | 101
8/9/2025 01:15 | 12 | 19 | 2.75 | 7.735 | 3.386 | 7.12 | 57 | 1.98 | 68.9 | 0.296 | 0.023 | 40.71 | 9754 | 8.34 | 59 |  | 181.21 | 3.37 | 6.85 | -3.109 | 0.25 | 101
8/9/2025 01:30 | 13 | 19 | 2.75 | 7.746 | 3.358 | 7.12 | 57 | 1.98 | 68.9 | 0.296 | 0.023 | 40.71 | 9754 | 8.34 | 59 |  | 181.13 | 3.37 | 6.85 | -3.109 | 0.25 | 100
8/9/2025 01:45 | 13 | 19 | 2.75 | 7.684 | 3.304 | 7.12 | 57 | 1.98 | 68.9 | 0.296 | 0.023 | 40.71 | 9754 | 8.33 | 59 |  | 181.05 | 3.39 | 6.85 | -3.109 | 0.28 | 101
8/9/2025 02:00 | 12 | 19 | 2.75 | 7.35 | 3.237 | 7.12 | 57 | 1.98 | 68.9 | 0.296 | 0.023 | 40.71 | 9754 | 8.33 | 58 |  | 178.91 | 3.51 | 6.85 | -3.109 | 0.31 | 101
8/9/2025 02:15 | 12 | 19 | 2.75 | 7.399 | 3.413 | 7.12 | 57 | 1.98 | 68.9 | 0.296 | 0.023 | 40.71 | 9754 | 8.33 | 58 |  | 178.97 | 3.48 | 6.87 | -3.109 | 0.26 | 101
8/9/2025 02:30 | 11 | 19 | 2.75 | 7.857 | 3.516 | 7.12 | 57 | 1.98 | 68.9 | 0.296 | 0.023 | 40.71 | 9754 | 8.32 | 58 |  | 180.76 | 3.31 | 6.85 | -3.109 | 0.26 | 101
8/9/2025 02:45 | 11 | 19 | 2.75 | 7.916 | 3.576 | 7.11 | 57 | 1.98 | 68.9 | 0.296 | 0.023 | 40.71 | 9754 | 8.32 | 58 |  | 181.02 | 3.29 | 6.83 | -3.109 | 0.31 | 101
8/9/2025 03:00 | 12 | 19 | 2.75 | 7.897 | 3.545 | 7.1 | 57 | 1.98 | 68.9 | 0.296 | 0.023 | 40.71 | 9754 | 8.32 | 58 |  | 181.4 | 3.31 | 6.83 | -3.109 | 0.26 | 101
8/9/2025 03:15 | 12 | 19 | 2.75 | 7.935 | 3.796 | 7.1 | 57 | 1.98 | 68.9 | 0.296 | 0.023 | 40.71 | 9754 | 8.31 | 58 |  | 180.68 | 3.28 | 6.82 | -3.109 | 0.26 | 101
8/9/2025 03:30 | 10 | 19 | 2.75 | 7.9 | 3.744 | 7.09 | 57 | 1.98 | 68.9 | 0.296 | 0.023 | 40.71 | 9754 | 8.31 | 58 |  | 180.74 | 3.29 | 6.83 | -3.109 | 0.28 | 101
8/9/2025 03:45 | 9 | 19 | 2.75 | 7.871 | 3.629 | 7.1 | 57 | 1.98 | 68.9 | 0.296 | 0.023 | 40.71 | 9754 | 8.3 | 58 |  | 180.87 | 3.31 | 6.84 | -3.109 | 0.26 | 101
8/9/2025 04:00 | 10 | 19 | 2.75 | 7.262 | 3.663 | 7.1 | 57 | 1.98 | 68.9 | 0.357 | 0.023 | 40.71 | 9754 | 8.3 | 58 |  | 176.92 | 3.51 | 6.85 | -3.109 | 0.25 | 101
8/9/2025 04:15 | 13 | 19 | 2.75 | 7.283 | 3.513 | 7.11 | 57 | 1.98 | 68.9 | 0.357 | 0.023 | 40.71 | 9754 | 8.3 | 58 |  | 177.02 | 3.5 | 6.87 | -3.109 | 0.26 | 100
8/9/2025 04:30 | 9 | 19 | 2.75 | 8 | 3.422 | 7.12 | 57 | 1.98 | 68.9 | 0.357 | 0.023 | 40.71 | 9754 | 8.3 | 58 |  | 180.62 | 3.25 | 6.86 | -3.109 | 0.28 | 101
8/9/2025 04:45 | 11 | 19 | 2.75 | 8.021 | 3.445 | 7.12 | 57 | 1.98 | 68.9 | 0.357 | 0.024 | 40.71 | 9754 | 8.3 | 58 |  | 180.73 | 3.24 | 6.85 | -3.109 | 0.28 | 101
8/9/2025 05:00 | 10 | 19 | 2.75 | 8.024 | 3.39 | 7.12 | 57 | 1.98 | 68.9 | 0.357 | 0.023 | 40.71 | 9754 | 8.3 | 58 |  | 180.33 | 3.24 | 6.85 | -3.109 | 0.26 | 101
8/9/2025 05:15 | 8 | 19 | 2.75 | 8.025 | 3.389 | 7.11 | 57 | 1.98 | 68.9 | 0.357 | 0.023 | 40.71 | 9754 | 8.3 | 58 |  | 180.25 | 3.23 | 6.85 | -3.109 | 0.24 | 101
8/9/2025 05:30 | 13 | 19 | 2.75 | 7.993 | 3.407 | 7.11 | 57 | 1.98 | 68.9 | 0.357 | 0.023 | 40.71 | 9754 | 8.29 | 58 |  | 180.36 | 3.25 | 6.84 | -3.109 | 0.27 | 101
8/9/2025 05:45 | 12 | 19 | 2.75 | 7.831 | 3.398 | 7.11 | 57 | 1.98 | 68.9 | 0.357 | 0.023 | 40.71 | 9754 | 8.29 | 58 |  | 180.47 | 3.32 | 6.84 | -3.109 | 0.25 | 101
8/9/2025 06:00 | 11 | 19 | 2.75 | 7.62 | 3.408 | 7.1 | 57 | 1.98 | 68.7 | 0.357 | 0.023 | 40.71 | 9754 | 8.3 | 58 |  | 180.59 | 3.41 | 6.84 | -3.109 | 0.3 | 101
8/9/2025 06:15 | 11 | 19 | 2.75 | 7.881 | 3.393 | 7.1 | 57 | 1.98 | 68.7 | 0.357 | 0.023 | 40.71 | 9754 | 8.3 | 58 |  | 179.88 | 3.29 | 6.84 | -3.109 | 0.27 | 101
8/9/2025 06:30 | 11 | 19 | 2.75 | 8.113 | 3.55 | 7.1 | 57 | 1.98 | 68.7 | 0.357 | 0.023 | 40.71 | 9754 | 8.29 | 58 |  | 180 | 3.19 | 6.84 | -3.109 | 0.25 | 101
8/9/2025 06:45 | 11 | 19 | 2.75 | 8.165 | 3.547 | 7.11 | 57 | 1.98 | 68.7 | 0.357 | 0.023 | 40.71 | 9754 | 8.29 | 58 |  | 180.3 | 3.18 | 6.83 | -3.109 | 0.26 | 101
8/9/2025 07:00 | 11 | 19 | 2.75 | 8.148 | 3.714 | 7.11 | 57 | 1.98 | 68.7 | 0.357 | 0.023 | 40.71 | 9754 | 8.28 | 58 |  | 179.98 | 3.18 | 6.84 | -3.109 | 0.26 | 101
8/9/2025 07:15 | 10 | 19 | 2.75 | 7.605 | 3.426 | 7.11 | 57 | 1.98 | 68.7 | 0.357 | 0.023 | 39.9 | 9662 | 8.28 | 58 |  | 179.86 | 3.41 | 6.85 | -3.109 | 0.29 | 101
8/9/2025 07:30 | 12 | 19 | 2.75 | 7.661 | 3.421 | 7.12 | 57 | 1.98 | 68.7 | 0.357 | 0.023 | 39.9 | 9662 | 8.28 | 58 |  | 180.42 | 3.39 | 6.86 | -3.109 | 0.29 | 101
8/9/2025 07:45 | 10 | 19 | 2.75 | 7.953 | 3.394 | 7.12 | 57 | 1.98 | 68.7 | 0.357 | 0.024 | 39.9 | 9662 | 8.28 | 58 |  | 179.81 | 3.26 | 6.86 | -3.109 | 0.28 | 101
8/9/2025 08:00 | 9 | 19 | 2.75 | 7.974 | 3.564 | 7.12 | 57 | 1.98 | 68.7 | 0.379 | 0.024 | 39.9 | 9662 | 8.27 | 58 |  | 180.03 | 3.25 | 6.85 | -3.109 | 0.27 | 101
8/9/2025 08:15 | 10 | 19 | 2.75 | 7.923 | 3.538 | 7.12 | 57 | 1.98 | 68.7 | 0.379 | 0.024 | 39.9 | 9662 | 8.26 | 58 |  | 180.31 | 3.28 | 6.85 | -3.109 | 0.3 | 101
8/9/2025 08:30 | 10 | 19 | 2.75 | 7.973 | 3.462 | 7.13 | 57 | 1.98 | 68.7 | 0.379 | 0.024 | 39.9 | 9662 | 8.24 | 58 |  | 179.7 | 3.25 | 6.87 | -3.109 | 0.28 | 101
8/9/2025 08:45 | 10 | 19 | 2.75 | 7.953 | 3.502 | 7.13 | 57 | 1.98 | 68.7 | 0.379 | 0.024 | 39.9 | 9662 | 8.26 | 58 |  | 180.41 | 3.27 | 6.87 | -3.109 | 0.26 | 101
8/9/2025 09:00 | 10 | 19 | 2.75 | 7.954 | 3.476 | 7.13 | 57 | 1.98 | 68.7 | 0.379 | 0.023 | 39.9 | 9662 | 8.28 | 58 |  | 180.09 | 3.26 | 6.87 | -3.109 | 0.29 | 101
8/9/2025 09:15 | 11 | 19 | 2.75 | 7.892 | 3.685 | 7.13 | 57 | 1.98 | 68.7 | 0.379 | 0.023 | 39.9 | 9662 | 8.3 | 58 |  | 177.79 | 3.24 | 6.87 | -3.109 | 0.27 | 101
8/9/2025 09:30 | 10 | 19 | 2.75 | 7.225 | 5.903 | 7.12 | 57 | 1.98 | 68.7 | 0.379 | 0.023 | 39.9 | 9662 | 8.31 | 58 |  | 175.54 | 3.5 | 6.89 | -3.109 | 0.27 | 101
8/9/2025 09:45 | 10 | 19 | 2.75 | 7.299 | 4.212 | 7.12 | 57 | 1.98 | 68.7 | 0.379 | 0.023 | 39.9 | 9662 | 8.31 | 58 |  | 176.87 | 3.49 | 6.88 | -3.109 | 0.23 | 101
8/9/2025 10:00 | 6 | 19 | 2.75 | 7.569 | 3.768 | 7.12 | 55 | 1.98 | 68.9 | 0.379 | 0.023 | 39.9 | 9662 | 8.31 | 58 |  | 177.67 | 3.38 | 6.87 | -3.109 | 0.23 | 101
8/9/2025 10:15 | 9 | 19 | 2.75 | 7.539 | 3.655 | 7.12 | 55 | 1.98 | 68.9 | 0.379 | 0.023 | 39.9 | 9662 | 8.31 | 58 |  | 177.75 | 3.4 | 6.87 | -3.109 | 0.32 | 101
8/9/2025 10:30 | 10 | 19 | 2.75 | 7.538 | 3.864 | 7.11 | 55 | 1.98 | 68.9 | 0.379 | 0.023 | 39.9 | 9662 | 8.31 | 58 |  | 177.66 | 3.39 | 6.86 | -3.109 | 0.26 | 101
8/9/2025 10:45 | 9 | 19 | 2.75 | 7.489 | 4.002 | 7.1 | 55 | 1.98 | 68.9 | 0.379 | 0.023 | 39.9 | 9662 | 8.31 | 58 |  | 177.32 | 3.41 | 6.85 | -3.109 | 0.25 | 101
8/9/2025 11:00 | 8 | 19 | 2.75 | 7.509 | 3.773 | 7.1 | 55 | 1.98 | 68.9 | 0.379 | 0.023 | 39.9 | 9662 | 8.31 | 58 |  | 177.63 | 3.41 | 6.79 | -3.109 | 0.28 | 101
8/9/2025 11:15 | 9 | 19 | 2.75 | 7.532 | 3.51 | 7.13 | 55 | 1.98 | 68.9 | 0.379 | 0.023 | 39.9 | 9662 | 8.3 | 58 |  | 177.51 | 3.39 | 6.78 | -3.109 | 0.24 | 101
8/9/2025 11:30 | 14 | 19 | 2.75 | 7.537 | 2.665 | 7.06 | 55 | 1.98 | 68.9 | 0.379 | 0.023 | 39.9 | 9662 | 8.3 | 58 |  | 177.54 | 3.39 | 6.8 | -3.109 | 0.23 | 100
8/9/2025 11:45 | 13 | 19 | 2.75 | 7.516 | 2.762 | 7.1 | 55 | 1.98 | 68.9 | 0.379 | 0.023 | 39.9 | 9662 | 8.3 | 58 |  | 177.72 | 3.4 | 6.87 | -3.109 | 0.31 | 100
8/9/2025 12:00 | 11 | 19 | 2.75 | 7.532 | 2.749 | 7.13 | 55 | 1.98 | 68.9 | 0.261 | 0.023 | 39.9 | 9662 | 8.3 | 58 |  | 177.68 | 3.4 | 6.87 | -3.109 | 0.28 | 101
8/9/2025 12:15 | 10 | 19 | 2.75 | 7.771 | 2.785 | 7.14 | 55 | 1.98 | 68.9 | 0.261 | 0.023 | 39.9 | 9662 | 8.29 | 58 |  | 177.47 | 3.29 | 6.86 | -3.109 | 0.26 | 101
8/9/2025 12:30 | 13 | 19 | 2.75 | 7.754 | 2.833 | 7.14 | 55 | 1.98 | 68.9 | 0.261 | 0.023 | 39.9 | 9662 | 8.29 | 58 |  | 177.03 | 3.29 | 6.86 | -3.109 | 0.25 | 100
8/9/2025 12:45 | 12 | 19 | 2.75 | 7.755 | 2.763 | 7.15 | 55 | 1.98 | 68.9 | 0.261 | 0.023 | 39.9 | 9662 | 8.3 | 58 |  | 176.68 | 3.28 | 6.87 | -3.109 | 0.26 | 101
8/9/2025 13:00 | 13 | 19 | 2.75 | 7.746 | 2.719 | 7.15 | 55 | 1.98 | 68.9 | 0.261 | 0.023 | 39.9 | 9662 | 8.3 | 58 |  | 177.49 | 3.3 | 6.87 | -3.109 | 0.28 | 101
8/9/2025 13:15 | 13 | 19 | 2.75 | 7.752 | 2.698 | 7.15 | 55 | 1.98 | 68.9 | 0.261 | 0.023 | 39.9 | 9662 | 8.29 | 58 |  | 177.55 | 3.3 | 6.86 | -3.109 | 0.26 | 100
8/9/2025 13:30 | 14 | 19 | 2.75 | 7.766 | 2.719 | 7.15 | 55 | 1.98 | 68.9 | 0.261 | 0.023 | 39.9 | 9662 | 8.29 | 58 |  | 177.51 | 3.29 | 6.86 | -3.109 | 0.27 | 100
8/9/2025 13:45 | 13 | 19 | 2.75 | 7.37 | 2.768 | 7.14 | 55 | 1.98 | 68.9 | 0.261 | 0.023 | 39.9 | 9662 | 8.29 | 58 |  | 177.9 | 3.48 | 6.86 | -3.109 | 0.27 | 101
8/9/2025 14:00 | 14 | 19 | 2.75 | 7.164 | 2.737 | 7.14 | 55 | 1.98 | 69 | 0.261 | 0.023 | 39.9 | 9662 | 8.29 | 57 |  | 174.63 | 3.51 | 6.87 | -3.109 | 0.25 | 100
8/9/2025 14:15 | 12 | 19 | 2.75 | 7.448 | 2.714 | 7.14 | 55 | 1.98 | 69 | 0.261 | 0.023 | 39.9 | 9662 | 8.29 | 57 |  | 177.59 | 3.43 | 6.86 | -3.109 | 0.27 | 101
8/9/2025 14:30 | 11 | 19 | 2.75 | 7.425 | 2.633 | 7.14 | 55 | 1.98 | 69 | 0.261 | 0.023 | 39.9 | 9662 | 8.29 | 57 |  | 178.32 | 3.46 | 6.86 | -3.109 | 0.26 | 101
8/9/2025 14:45 | 11 | 19 | 2.75 | 7.45 | 2.655 | 7.15 | 55 | 1.98 | 69 | 0.261 | 0.023 | 39.9 | 9662 | 8.28 | 57 |  | 177.62 | 3.43 | 6.86 | -3.109 | 0.26 | 101
8/9/2025 15:00 | 10 | 19 | 2.75 | 7.425 | 2.647 | 7.15 | 55 | 1.98 | 69 | 0.261 | 0.023 | 39.9 | 9662 | 8.28 | 57 |  | 179.01 | 3.47 | 6.86 | -3.109 | 0.27 | 101
8/9/2025 15:15 | 14 | 19 | 2.75 | 7.405 | 3.108 | 7.21 | 55 | 1.98 | 69 | 0.261 | 0.023 | 39.9 | 9662 | 8.27 | 57 |  | 0 | 0 | 6.87 | -3.109 | 0.27 | 100
8/9/2025 15:30 | 11 | 19 | 2.75 | 7.46 | 3.132 | 7.22 | 55 | 1.98 | 69 | 0.261 | 0.023 | 39.9 | 9662 | 8.27 | 57 |  | 0 | 0 | 6.87 | -3.109 | 0.26 | 101
8/9/2025 15:45 | 11 | 19 | 2.75 | 7.451 | 3.514 | 7.21 | 55 | 1.98 | 69 | 0.261 | 0.023 | 39.9 | 9662 | 8.28 | 57 |  | 0 | 0 | 6.86 | -3.109 | 0.26 | 101
8/9/2025 16:00 | 9 | 19 | 2.75 | 7.739 | 3.828 | 7.2 | 55 | 1.98 | 69 | 0.208 | 0.023 | 39.9 | 9662 | 8.28 | 57 |  | 180.53 | 3.36 | 6.85 | -3.109 | 0.27 | 101
8/9/2025 16:15 | 9 | 19 | 2.75 | 7.735 | 10.53 | 7.13 | 55 | 1.98 | 69 | 0.208 | 0.023 | 36.81 | 8854 | 8.28 | 57 |  | 181.11 | 3.37 | 6.83 | -3.109 | 0.24 | 101
8/9/2025 16:30 | 14 | 19 | 2.75 | 7.691 | 3.742 | 7.12 | 55 | 1.98 | 69 | 0.208 | 0.023 | 36.81 | 8854 | 8.28 | 57 |  | 181.24 | 3.39 | 6.82 | -3.109 | 0.26 | 101
8/9/2025 16:45 | 12 | 19 | 2.75 | 7.742 | 3.312 | 7.13 | 55 | 1.98 | 69 | 0.208 | 0.023 | 36.81 | 8854 | 8.28 | 57 |  | 181.51 | 3.38 | 6.83 | -3.109 | 0.26 | 101
8/9/2025 17:00 | 15 | 19 | 2.75 | 7.723 | 3.283 | 7.13 | 55 | 1.98 | 69 | 0.208 | 0.023 | 36.81 | 8854 | 8.28 | 57 |  | 181.26 | 3.38 | 6.84 | -3.109 | 0.26 | 99
8/9/2025 17:15 | 15 | 19 | 2.75 | 7.168 | 3.19 | 7.13 | 55 | 1.98 | 69 | 0.208 | 0.023 | 36.81 | 8854 | 8.28 | 57 |  | 174.47 | 3.5 | 6.85 | -3.109 | 0.27 | 100
8/9/2025 17:30 | 16 | 19 | 2.75 | 7.169 | 3.128 | 7.14 | 55 | 1.98 | 69 | 0.208 | 0.023 | 36.81 | 8854 | 8.27 | 57 |  | 174.47 | 3.5 | 6.89 | -3.109 | 0.26 | 100
8/9/2025 17:45 | 15 | 19 | 2.75 | 7.52 | 2.701 | 7.17 | 55 | 1.98 | 69 | 0.208 | 0.023 | 36.81 | 8854 | 8.28 | 57 |  | 180.87 | 3.46 | 6.89 | -3.109 | 0.26 | 100
8/9/2025 18:00 | 12 | 19 | 2.75 | 7.506 | 2.539 | 7.2 | 55 | 1.98 | 69.2 | 0.208 | 0.023 | 36.81 | 8854 | 8.28 | 57 |  | 181.73 | 3.49 | 6.91 | -3.109 | 0.26 | 101
8/9/2025 18:15 | 11 | 19 | 2.75 | 7.496 | 2.505 | 7.21 | 55 | 1.98 | 69.2 | 0.208 | 0.023 | 36.81 | 8854 | 8.29 | 57 |  | 181.46 | 3.49 | 6.91 | -3.109 | 0.26 | 101
8/9/2025 18:30 | 13 | 19 | 2.75 | 7.541 | 2.501 | 7.18 | 55 | 1.98 | 69.2 | 0.208 | 0.023 | 36.81 | 8854 | 8.29 | 57 |  | 180.93 | 3.45 | 6.89 | -3.109 | 0.27 | 100
8/9/2025 18:45 | 13 | 19 | 2.75 | 6.802 | 2.819 | 7.18 | 55 | 1.98 | 69.2 | 0.208 | 0.023 | 36.81 | 8854 | 8.29 | 57 |  | 166.29 | 3.52 | 6.89 | -3.109 | 0.27 | 100
8/9/2025 19:00 | 14 | 19 | 2.75 | 6.804 | 3.346 | 7.14 | 55 | 1.98 | 69.2 | 0.208 | 0.023 | 36.81 | 8854 | 8.3 | 57 |  | 165.51 | 3.5 | 6.86 | -3.109 | 0.3 | 100
8/9/2025 19:15 | 12 | 19 | 2.75 | 7.143 | 3.424 | 7.11 | 55 | 1.98 | 69.2 | 0.208 | 0.023 | 36.81 | 8854 | 8.3 | 57 |  | 173.55 | 3.5 | 6.83 | -3.109 | 0.25 | 101
8/9/2025 19:30 | 11 | 19 | 2.75 | 7.178 | 3.277 | 7.12 | 55 | 1.98 | 69.2 | 0.208 | 0.023 | 36.81 | 8854 | 8.3 | 57 |  | 174.04 | 3.49 | 6.83 | -3.109 | 0.26 | 101
8/9/2025 19:45 | 11 | 19 | 2.75 | 7.179 | 2.751 | 7.15 | 55 | 1.98 | 69.2 | 0.208 | 0.023 | 36.81 | 8854 | 8.31 | 57 |  | 174.39 | 3.5 | 6.85 | -3.109 | 0.27 | 101
8/9/2025 20:00 | 10 | 19 | 2.75 | 7.162 | 2.651 | 7.16 | 55 | 1.98 | 69.2 | 0.206 | 0.023 | 36.81 | 8854 | 8.31 | 57 |  | 173.37 | 3.49 | 6.87 | -3.109 | 0.26 | 101
8/9/2025 20:15 | 11 | 19 | 2.75 | 7.147 | 2.377 | 7.19 | 55 | 1.98 | 69.2 | 0.206 | 0.023 | 36.81 | 8854 | 8.31 | 57 |  | 174.11 | 3.51 | 6.9 | -3.109 | 0.25 | 101
8/9/2025 20:30 | 5 | 19 | 2.75 | 7.147 | 2.256 | 7.21 | 55 | 1.98 | 69.2 | 0.206 | 0.023 | 36.81 | 8854 | 8.31 | 57 |  | 173.69 | 3.5 | 6.91 | -3.109 | 0.25 | 101
8/9/2025 20:45 | 10 | 19 | 2.75 | 7.189 | 2.114 | 7.23 | 55 | 1.98 | 69.2 | 0.206 | 0.023 | 36.81 | 8854 | 8.32 | 57 |  | 175.04 | 3.51 | 6.93 | -3.109 | 0.25 | 101
8/9/2025 21:00 | 9 | 19 | 2.75 | 6.69 | 2.121 | 7.24 | 55 | 1.98 | 69.2 | 0.206 | 0.023 | 36.81 | 8854 | 8.31 | 57 |  | 161.7 | 3.48 | 6.94 | -3.109 | 0.26 | 101
8/9/2025 21:15 | 8 | 19 | 2.75 | 6.691 | 2.238 | 7.24 | 55 | 1.98 | 69.2 | 0.206 | 0.023 | 36.81 | 8854 | 8.32 | 57 |  | 162.13 | 3.49 | 6.94 | -3.109 | 0.24 | 101
8/9/2025 21:30 | 9 | 19 | 2.75 | 6.943 | 2.479 | 7.2 | 55 | 1.98 | 69.2 | 0.206 | 0.023 | 37.32 | 8991 | 8.32 | 57 |  | 169.09 | 3.51 | 6.9 | -3.109 | 0.26 | 101
8/9/2025 21:45 | 5 | 19 | 2.75 | 6.933 | 3.114 | 7.15 | 55 | 1.98 | 69.2 | 0.206 | 0.023 | 37.32 | 8991 | 8.33 | 57 |  | 167.92 | 3.49 | 6.84 | -3.109 | 0.24 | 101
8/9/2025 22:00 | 12 | 19 | 2.75 | 6.918 | 3.771 | 7.15 | 54 | 1.98 | 69.2 | 0.206 | 0.024 | 37.32 | 8991 | 8.34 | 57 |  | 0 | 0 | 6.82 | -3.109 | 0.25 | 101
8/9/2025 22:15 | 9 | 19 | 2.75 | 6.951 | 4.115 | 7.16 | 54 | 1.98 | 69.2 | 0.206 | 0.024 | 37.32 | 8991 | 8.34 | 57 |  | 0 | 0 | 6.81 | -3.109 | 0.24 | 101
8/9/2025 22:30 | 9 | 19 | 2.75 | 6.958 | 3.996 | 7.16 | 54 | 1.98 | 69.2 | 0.206 | 0.024 | 37.32 | 8991 | 8.34 | 57 |  | 0 | 0 | 6.8 | -3.109 | 0.25 | 101
8/9/2025 22:45 | 9 | 19 | 2.75 | 6.981 | 3.972 | 7.18 | 54 | 1.98 | 69.2 | 0.206 | 0.024 | 37.32 | 8991 | 8.33 | 57 |  | 0 | 0 | 6.81 | -3.109 | 0.25 | 101
8/9/2025 23:00 | 10 | 19 | 2.75 | 6.95 | 3.959 | 7.19 | 54 | 1.98 | 69.2 | 0.206 | 0.024 | 37.32 | 8991 | 8.31 | 57 |  | 0 | 0 | 6.84 | -3.109 | 0.25 | 101
8/9/2025 23:15 | 8 | 19 | 2.75 | 6.974 | 4.024 | 7.21 | 54 | 1.98 | 69.2 | 0.206 | 0.024 | 37.32 | 8991 | 8.3 | 57 |  | 0 | 0 | 6.85 | -3.109 | 0.26 | 101
8/9/2025 23:30 | 8 | 19 | 2.75 | 6.958 | 4.077 | 7.22 | 54 | 1.98 | 69.2 | 0.206 | 0.024 | 37.32 | 8991 | 8.32 | 57 |  | 0 | 0 | 6.87 | -3.109 | 0.26 | 101
8/9/2025 23:45 | 9 | 19 | 2.75 | 6.969 | 4.003 | 7.22 | 54 | 1.98 | 69.2 | 0.206 | 0.023 | 37.32 | 8991 | 8.34 | 57 |  | 0 | 0 | 6.88 | -3.109 | 0.3 | 101
8/10/2025 00:00 | 10 | 19 | 2.75 | 6.942 | 3.967 | 7.23 | 54 | 1.98 | 69.2 | 0.327 | 0.023 | 37.32 | 8991 | 8.36 | 57 |  | 0 | 0 | 6.87 | -3.109 | 0.26 | 101
8/10/2025 00:15 | 10 | 19 | 2.75 | 6.953 | 3.865 | 7.23 | 54 | 1.98 | 69.2 | 0.327 | 0.023 | 37.32 | 8991 | 8.37 | 57 |  | 0 | 0 | 6.89 | -3.109 | 0.26 | 101
8/10/2025 00:30 | 9 | 19 | 2.75 | 6.959 | 4.978 | 7.23 | 54 | 1.98 | 69.2 | 0.327 | 0.023 | 37.32 | 8991 | 8.38 | 57 |  | 168.83 | 3.49 | 6.88 | -3.109 | 0.27 | 101
8/10/2025 00:45 | 8 | 19 | 2.75 | 6.981 | 21.948 | 7.15 | 54 | 1.98 | 69.2 | 0.327 | 0.023 | 37.32 | 8991 | 8.38 | 57 |  | 169.2 | 3.49 | 6.86 | -3.109 | 0.25 | 101
8/10/2025 01:00 | 9 | 19 | 2.75 | 6.959 | 8.294 | 7.15 | 54 | 1.98 | 69.2 | 0.327 | 0.023 | 37.32 | 8991 | 8.39 | 57 |  | 169.44 | 3.51 | 6.85 | -3.109 | 0.24 | 101
8/10/2025 01:15 | 9 | 19 | 2.75 | 6.972 | 5.198 | 7.13 | 54 | 1.98 | 69.2 | 0.327 | 0.023 | 37.32 | 8991 | 8.39 | 57 |  | 169.74 | 3.51 | 6.84 | -3.109 | 0.25 | 101
8/10/2025 01:30 | 10 | 19 | 2.75 | 7.012 | 5.437 | 7.11 | 54 | 1.98 | 69.2 | 0.327 | 0.023 | 37.32 | 8991 | 8.39 | 57 |  | 169.74 | 3.49 | 6.83 | -3.109 | 0.23 | 101
8/10/2025 01:45 | 10 | 19 | 2.75 | 6.97 | 5.057 | 7.1 | 54 | 1.98 | 69.2 | 0.327 | 0.023 | 37.32 | 8991 | 8.39 | 57 |  | 169.66 | 3.51 | 6.82 | -3.109 | 0.23 | 101
8/10/2025 02:00 | 12 | 19 | 2.75 | 6.955 | 4.422 | 7.1 | 54 | 1.98 | 69 | 0.327 | 0.023 | 37.32 | 8991 | 8.39 | 57 |  | 168.84 | 3.5 | 6.83 | -3.109 | 0.24 | 101
8/10/2025 02:15 | 12 | 19 | 2.75 | 6.919 | 4.029 | 7.11 | 54 | 1.98 | 69 | 0.327 | 0.023 | 37.32 | 8991 | 8.39 | 57 |  | 168.09 | 3.5 | 6.85 | -3.109 | 0.25 | 101
8/10/2025 02:30 | 12 | 19 | 2.75 | 6.911 | 3.65 | 7.11 | 54 | 1.98 | 69 | 0.327 | 0.023 | 37.32 | 8991 | 8.38 | 57 |  | 167.42 | 3.49 | 6.85 | -3.109 | 0.28 | 101
8/10/2025 02:45 | 11 | 19 | 2.75 | 6.454 | 3.392 | 7.11 | 54 | 1.98 | 69 | 0.327 | 0.023 | 37.32 | 8991 | 8.38 | 57 |  | 157.27 | 3.51 | 6.86 | -3.109 | 0.25 | 101
8/10/2025 03:00 | 11 | 19 | 2.75 | 6.747 | 3.327 | 7.12 | 54 | 1.98 | 69 | 0.327 | 0.023 | 37.32 | 8991 | 8.38 | 57 |  | 164.09 | 3.5 | 6.9 | -3.109 | 0.25 | 101
8/10/2025 03:15 | 10 | 19 | 2.75 | 6.74 | 3.237 | 7.12 | 54 | 1.98 | 69 | 0.327 | 0.023 | 37.32 | 8991 | 8.37 | 57 |  | 164.25 | 3.51 | 6.89 | -3.109 | 0.26 | 101
8/10/2025 03:30 | 13 | 19 | 2.75 | 6.774 | 3.175 | 7.12 | 54 | 1.98 | 69 | 0.327 | 0.023 | 37.32 | 8991 | 8.37 | 57 |  | 165.03 | 3.51 | 6.87 | -3.109 | 0.28 | 100
8/10/2025 03:45 | 11 | 19 | 2.75 | 6.753 | 3.124 | 7.12 | 54 | 1.98 | 69 | 0.327 | 0.023 | 37.32 | 8991 | 8.37 | 57 |  | 165.11 | 3.52 | 6.85 | -3.109 | 0.26 | 101
8/10/2025 04:00 | 10 | 19 | 2.75 | 6.765 | 3.155 | 7.12 | 54 | 1.98 | 69 | 0.25 | 0.023 | 37.32 | 8991 | 8.36 | 57 |  | 164.68 | 3.51 | 6.84 | -3.109 | 0.25 | 101
8/10/2025 04:15 | 12 | 19 | 2.75 | 6.786 | 3.287 | 7.11 | 54 | 1.98 | 69 | 0.25 | 0.023 | 37.32 | 8991 | 8.37 | 57 |  | 165.08 | 3.5 | 6.83 | -3.109 | 0.27 | 101
8/10/2025 04:30 | 10 | 19 | 2.75 | 6.774 | 3.31 | 7.1 | 54 | 1.98 | 69 | 0.25 | 0.023 | 37.32 | 8991 | 8.37 | 57 |  | 164.06 | 3.49 | 6.82 | -3.109 | 0.25 | 101
8/10/2025 04:45 | 11 | 19 | 2.75 | 6.63 | 3.455 | 7.09 | 54 | 1.98 | 69 | 0.25 | 0.023 | 37.32 | 8991 | 8.36 | 57 |  | 161.71 | 3.51 | 6.81 | -3.109 | 0.24 | 101
8/10/2025 05:00 | 11 | 19 | 2.75 | 6.665 | 3.555 | 7.09 | 54 | 1.98 | 69 | 0.25 | 0.023 | 37.32 | 8991 | 8.36 | 57 |  | 161.96 | 3.5 | 6.82 | -3.109 | 0.21 | 101
8/10/2025 05:15 | 8 | 19 | 2.75 | 6.944 | 3.568 | 7.08 | 54 | 1.98 | 69 | 0.25 | 0.022 | 37.32 | 8991 | 8.36 | 57 |  | 168.82 | 3.5 | 6.8 | -3.109 | 0.25 | 101
8/10/2025 05:30 | 8 | 19 | 2.75 | 6.914 | 3.503 | 7.09 | 54 | 1.98 | 69 | 0.25 | 0.023 | 37.55 | 8875 | 8.36 | 57 |  | 169.02 | 3.52 | 6.8 | -3.109 | 0.23 | 101
8/10/2025 05:45 | 8 | 19 | 2.75 | 6.914 | 3.405 | 7.09 | 54 | 1.98 | 69 | 0.25 | 0.024 | 37.55 | 8875 | 8.36 | 57 |  | 167.67 | 3.49 | 6.81 | -3.109 | 0.39 | 101
8/10/2025 06:00 | 10 | 19 | 2.75 | 6.91 | 3.351 | 7.1 | 54 | 1.98 | 68.9 | 0.25 | 0.024 | 37.55 | 8875 | 8.35 | 57 |  | 0 | 0 | 6.82 | -3.109 | 0.24 | 101
8/10/2025 06:15 | 9 | 19 | 2.75 | 6.869 | 3.828 | 7.14 | 54 | 1.98 | 68.9 | 0.25 | 0.025 | 37.55 | 8875 | 8.35 | 57 |  | 0 | 0 | 6.84 | -3.109 | 0.41 | 101
8/10/2025 06:30 | 7 | 19 | 2.75 | 6.913 | 3.781 | 7.16 | 54 | 1.98 | 68.9 | 0.25 | 0.024 | 37.55 | 8875 | 8.34 | 57 |  | 0 | 0 | 6.84 | -3.109 | 0.31 | 101
8/10/2025 06:45 | 8 | 19 | 2.75 | 6.906 | 3.768 | 7.17 | 54 | 1.98 | 68.9 | 0.25 | 0.024 | 37.55 | 8875 | 8.33 | 57 |  | 0 | 0 | 6.86 | -3.109 | 0.25 | 101
8/10/2025 07:00 | 8 | 19 | 2.75 | 6.926 | 3.797 | 7.18 | 54 | 1.98 | 68.9 | 0.25 | 0.024 | 37.55 | 8875 | 8.33 | 57 |  | 0 | 0 | 6.86 | -3.109 | 0.25 | 101
8/10/2025 07:15 | 6 | 19 | 2.75 | 7.186 | 3.73 | 7.19 | 54 | 1.98 | 68.9 | 0.25 | 0.024 | 37.55 | 8875 | 8.35 | 57 |  | 0 | 0 | 6.85 | -3.109 | 0.25 | 101
8/10/2025 07:30 | 7 | 19 | 2.75 | 7.211 | 3.742 | 7.2 | 54 | 1.98 | 68.9 | 0.25 | 0.024 | 37.55 | 8875 | 8.38 | 57 |  | 0 | 0 | 6.86 | -3.109 | 0.26 | 101
8/10/2025 07:45 | 6 | 19 | 2.75 | 7.181 | 3.967 | 7.19 | 54 | 1.98 | 68.9 | 0.25 | 0.024 | 37.55 | 8875 | 8.39 | 57 |  | 0 | 0 | 6.86 | -3.109 | 0.34 | 101
8/10/2025 08:00 | 4 | 19 | 2.75 | 7.204 | 4.116 | 7.19 | 54 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.39 | 57 |  | 0 | 0 | 6.86 | -3.109 | 0.25 | 101
8/10/2025 08:15 | 6 | 19 | 2.75 | 7.159 | 4.32 | 7.17 | 54 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.39 | 57 |  | 0 | 0 | 6.85 | -3.109 | 0.26 | 101
8/10/2025 08:30 | 7 | 19 | 2.75 | 7.162 | 4.633 | 7.16 | 54 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.38 | 57 |  | 0 | 0 | 6.84 | -3.109 | 0.25 | 101
8/10/2025 08:45 | 3 | 19 | 2.75 | 6.678 | 4.877 | 7.14 | 54 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.37 | 57 |  | 0 | 0 | 6.85 | -3.109 | 0.24 | 101
8/10/2025 09:00 | 0 | 19 | 2.75 | 6.961 | 5.006 | 7.14 | 54 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.36 | 57 |  | 0 | 0 | 6.84 | -3.109 | 0.29 | 101
8/10/2025 09:15 | 4 | 19 | 2.75 | 7.32 | 4.553 | 7.09 | 54 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.35 | 57 |  | 178.38 | 3.51 | 6.83 | -3.109 | 0.25 | 101
8/10/2025 09:30 | 7 | 19 | 2.75 | 7.347 | 4.715 | 7.1 | 54 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.35 | 57 |  | 178.26 | 3.49 | 6.83 | -3.109 | 0.26 | 101
8/10/2025 09:45 | 6 | 19 | 2.75 | 7.313 | 4.032 | 7.11 | 54 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.34 | 57 |  | 177.98 | 3.5 | 6.85 | -3.109 | 0.29 | 101
8/10/2025 10:00 | 5 | 19 | 2.75 | 7.305 | 3.851 | 7.11 | 56 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.34 | 57 |  | 177.93 | 3.51 | 6.86 | -3.109 | 0.26 | 101
8/10/2025 10:15 | 4 | 19 | 2.75 | 6.791 | 3.735 | 7.12 | 56 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.34 | 57 |  | 165.67 | 3.51 | 6.88 | -3.109 | 0.28 | 101
8/10/2025 10:30 | 5 | 19 | 2.75 | 6.886 | 3.42 | 7.14 | 56 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.34 | 57 |  | 166.87 | 3.49 | 6.9 | -3.109 | 0.34 | 101
8/10/2025 10:45 | 0 | 19 | 2.75 | 7.061 | 3.176 | 7.14 | 56 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.34 | 57 |  | 170.85 | 3.48 | 6.89 | -3.109 | 0.24 | 101
8/10/2025 11:00 | 2 | 19 | 2.75 | 7.02 | 3.068 | 7.15 | 56 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.35 | 57 |  | 170.64 | 3.5 | 6.89 | -3.109 | 0.27 | 101
8/10/2025 11:15 | 2 | 19 | 2.75 | 7.05 | 2.976 | 7.15 | 56 | 1.98 | 68.9 | 0.332 | 0.024 | 37.55 | 8875 | 8.35 | 57 |  | 170.81 | 3.49 | 6.89 | -3.109 | 0.45 | 101
8/10/2025 11:30 | 2 | 19 | 2.75 | 7.005 | 2.168 | 7.12 | 56 | 1.98 | 68.9 | 0.332 | 0.023 | 37.55 | 8875 | 8.36 | 57 |  | 171.1 | 3.52 | 6.81 | -3.109 | 0.28 | 101
8/10/2025 11:45 | 2 | 19 | 2.75 | 7.038 | 2.174 | 7.15 | 56 | 1.98 | 68.9 | 0.332 | 0.023 | 37.55 | 8875 | 8.36 | 57 |  | 170.62 | 3.49 | 6.83 | -3.109 | 0.26 | 101
8/10/2025 12:00 | 3 | 19 | 2.75 | 7.023 | 2.225 | 7.17 | 56 | 1.98 | 68.9 | 0.175 | 0.023 | 37.55 | 8875 | 8.37 | 57 |  | 170.64 | 3.5 | 6.84 | -3.109 | 0.21 | 101
8/10/2025 12:15 | 5 | 19 | 2.75 | 7.047 | 2.349 | 7.17 | 56 | 1.98 | 68.9 | 0.175 | 0.023 | 37.55 | 8875 | 8.37 | 57 |  | 170.9 | 3.49 | 6.89 | -3.109 | 0.23 | 101
8/10/2025 12:30 | 9 | 19 | 2.75 | 7.315 | 2.42 | 7.15 | 56 | 1.98 | 68.9 | 0.175 | 0.023 | 37.55 | 8875 | 8.38 | 57 |  | 177.4 | 3.49 | 6.89 | -3.109 | 0.25 | 101
8/10/2025 12:45 | 7 | 19 | 2.75 | 7.28 | 2.609 | 7.15 | 56 | 1.98 | 68.9 | 0.175 | 0.023 | 37.81 | 8796 | 8.39 | 57 |  | 177.41 | 3.51 | 6.88 | -3.109 | 0.29 | 101
8/10/2025 13:00 | 7 | 19 | 2.75 | 7.587 | 2.614 | 7.15 | 56 | 1.98 | 68.9 | 0.175 | 0.024 | 37.81 | 8796 | 8.39 | 57 |  | 181.21 | 3.44 | 6.88 | -3.109 | 0.29 | 101
8/10/2025 13:15 | 9 | 19 | 2.75 | 7.584 | 2.691 | 7.14 | 56 | 1.98 | 68.9 | 0.175 | 0.024 | 37.81 | 8796 | 8.39 | 57 |  | 181.27 | 3.44 | 6.86 | -3.109 | 0.3 | 101
8/10/2025 13:30 | 13 | 19 | 2.75 | 7.542 | 2.9 | 7.13 | 56 | 1.98 | 68.9 | 0.175 | 0.025 | 37.81 | 8796 | 8.39 | 57 |  | 181.14 | 3.46 | 6.85 | -3.109 | 0.29 | 101
8/10/2025 13:45 | 11 | 19 | 2.75 | 7.004 | 2.94 | 7.13 | 56 | 1.98 | 68.9 | 0.175 | 0.025 | 37.81 | 8796 | 8.38 | 57 |  | 170.71 | 3.51 | 6.86 | -3.109 | 0.3 | 101
8/10/2025 14:00 | 10 | 19 | 2.75 | 7.022 | 2.752 | 7.14 | 56 | 1.98 | 69.2 | 0.175 | 0.025 | 37.81 | 8796 | 8.38 | 57 |  | 171.49 | 3.52 | 6.87 | -3.109 | 0.27 | 101
8/10/2025 14:15 | 10 | 19 | 2.75 | 7.406 | 2.641 | 7.15 | 56 | 1.98 | 69.2 | 0.175 | 0.025 | 37.81 | 8796 | 8.38 | 57 |  | 179.69 | 3.49 | 6.87 | -3.109 | 0.31 | 101
8/10/2025 14:30 | 11 | 19 | 2.75 | 7.372 | 2.493 | 7.15 | 56 | 1.98 | 69.2 | 0.175 | 0.025 | 37.81 | 8796 | 8.41 | 57 |  | 179.14 | 3.5 | 6.87 | -3.109 | 0.29 | 101
8/10/2025 14:45 | 11 | 19 | 2.75 | 7.415 | 2.458 | 7.16 | 56 | 1.98 | 69.2 | 0.175 | 0.025 | 37.81 | 8796 | 8.43 | 57 |  | 179.6 | 3.49 | 6.87 | -3.109 | 0.31 | 101
8/10/2025 15:00 | 9 | 19 | 2.75 | 7.397 | 2.585 | 7.15 | 56 | 1.98 | 69.2 | 0.175 | 0.026 | 37.81 | 8796 | 8.43 | 57 |  | 179.87 | 3.5 | 6.86 | -3.109 | 0.28 | 101
8/10/2025 15:15 | 1 | 19 | 2.75 | 7.373 | 2.745 | 7.14 | 56 | 1.98 | 69.2 | 0.175 | 0.025 | 37.81 | 8796 | 8.42 | 57 |  | 180.06 | 3.52 | 6.84 | -3.109 | 0.29 | 101
8/10/2025 15:30 | 9 | 19 | 2.75 | 7.365 | 2.657 | 7.15 | 56 | 1.98 | 69.2 | 0.175 | 0.025 | 37.81 | 8796 | 8.4 | 57 |  | 179.08 | 3.5 | 6.86 | -3.109 | 0.3 | 101
8/10/2025 15:45 | 7 | 19 | 2.75 | 7.313 | 2.683 | 7.15 | 56 | 1.98 | 69.2 | 0.175 | 0.025 | 37.81 | 8796 | 8.38 | 57 |  | 178.46 | 3.51 | 6.86 | -3.109 | 0.28 | 101
8/10/2025 16:00 | 10 | 19 | 2.75 | 6.908 | 2.762 | 7.15 | 56 | 1.98 | 69.2 | 0.183 | 0.025 | 37.81 | 8796 | 8.37 | 57 |  | 168.04 | 3.5 | 6.86 | -3.109 | 0.3 | 101
8/10/2025 16:15 | 9 | 19 | 2.75 | 7.487 | 2.691 | 7.14 | 56 | 1.98 | 69.2 | 0.183 | 0.025 | 37.81 | 8796 | 8.35 | 57 |  | 181.04 | 3.48 | 6.85 | -3.109 | 0.29 | 101
8/10/2025 16:30 | 7 | 19 | 2.75 | 7.48 | 2.672 | 7.14 | 56 | 1.98 | 69.2 | 0.183 | 0.025 | 37.81 | 8796 | 8.35 | 57 |  | 181.54 | 3.49 | 6.85 | -3.109 | 0.29 | 101
8/10/2025 16:45 | 6 | 19 | 2.75 | 7.466 | 2.739 | 7.15 | 56 | 1.98 | 69.2 | 0.183 | 0.025 | 37.81 | 8796 | 8.35 | 57 |  | 180.65 | 3.48 | 6.85 | -3.109 | 0.29 | 101
8/10/2025 17:00 | 11 | 19 | 2.75 | 7.496 | 2.709 | 7.17 | 56 | 1.98 | 69.2 | 0.183 | 0.025 | 37.81 | 8796 | 8.35 | 57 |  | 181.66 | 3.49 | 6.88 | -3.109 | 0.28 | 101
8/10/2025 17:15 | 10 | 19 | 2.75 | 7.425 | 3.019 | 7.23 | 56 | 1.98 | 69.2 | 0.183 | 0.025 | 37.81 | 8796 | 8.34 | 57 |  | 0 | 0 | 6.88 | -3.109 | 0.29 | 101
8/10/2025 17:30 | -2 | 19 | 2.75 | 7.029 | 2.938 | 7.24 | 56 | 1.98 | 69.2 | 0.183 | 0.025 | 37.81 | 8796 | 8.33 | 57 |  | 0 | 0 | 6.9 | -3.109 | 0.29 | 101
8/10/2025 17:45 | 6 | 19 | 2.75 | 7.61 | 3.16 | 7.25 | 56 | 1.98 | 69.2 | 0.183 | 0.025 | 37.81 | 8796 | 8.33 | 57 |  | 179.36 | 3.39 | 6.91 | -3.109 | 0.29 | 101
8/10/2025 18:00 | 7 | 19 | 2.75 | 7.675 | 39.937 | 7.17 | 56 | 1.98 | 69.4 | 0.183 | 0.025 | 38.19 | 8839 | 8.33 | 57 |  | 179.02 | 3.36 | 6.88 | -3.109 | 0.33 | 101
8/10/2025 18:15 | 6 | 19 | 2.75 | 7.89 | 39.937 | 7.17 | 56 | 1.98 | 69.4 | 0.183 | 0.025 | 38.19 | 8839 | 8.33 | 57 |  | 0 | 0 | 6.86 | -3.109 | 0.32 | 101
8/10/2025 18:30 | 4 | 19 | 2.75 | 7.85 | 4.804 | 7.25 | 56 | 1.98 | 69.4 | 0.183 | 0.026 | 38.19 | 8839 | 8.33 | 57 |  | 0 | 0 | 6.87 | -3.109 | 0.3 | 101
8/10/2025 18:45 | 8 | 19 | 2.75 | 7.828 | 3.864 | 7.28 | 56 | 1.98 | 69.4 | 0.183 | 0.027 | 38.19 | 8839 | 8.33 | 57 |  | 0 | 0 | 6.87 | -3.109 | 0.3 | 101
8/10/2025 19:00 | 7 | 19 | 2.75 | 7.819 | 3.713 | 7.3 | 56 | 1.98 | 69.4 | 0.183 | 0.027 | 38.19 | 8839 | 8.33 | 57 |  | 0 | 0 | 6.88 | -3.109 | 0.3 | 101
8/10/2025 19:15 | 6 | 19 | 2.75 | 7.837 | 3.252 | 7.29 | 56 | 1.98 | 69.4 | 0.183 | 0.027 | 38.19 | 8839 | 8.32 | 57 |  | 179.12 | 3.29 | 6.88 | -3.109 | 0.29 | 101
8/10/2025 19:30 | 7 | 19 | 2.75 | 7.881 | 5.684 | 7.22 | 56 | 1.98 | 69.4 | 0.183 | 0.027 | 38.19 | 8839 | 8.34 | 57 |  | 179.54 | 3.28 | 6.88 | -3.109 | 0.3 | 101
8/10/2025 19:45 | 9 | 19 | 2.75 | 7.808 | 3.755 | 7.21 | 56 | 1.98 | 69.4 | 0.183 | 0.027 | 38.19 | 8839 | 8.37 | 57 |  | 179.14 | 3.3 | 6.87 | -3.109 | 0.28 | 101
8/10/2025 20:00 | 10 | 19 | 2.75 | 7.824 | 2.954 | 7.21 | 56 | 1.98 | 69.4 | 0.212 | 0.027 | 38.19 | 8839 | 8.39 | 57 |  | 179.58 | 3.31 | 6.88 | -3.109 | 0.27 | 101
8/10/2025 20:15 | 8 | 19 | 2.75 | 7.854 | 2.716 | 7.22 | 56 | 1.98 | 69.4 | 0.212 | 0.027 | 38.19 | 8839 | 8.39 | 57 |  | 179.05 | 3.28 | 6.91 | -3.109 | 0.25 | 101
8/10/2025 20:30 | 5 | 19 | 2.75 | 7.858 | 2.833 | 7.22 | 56 | 1.98 | 69.4 | 0.212 | 0.026 | 38.19 | 8839 | 8.38 | 57 |  | 179.33 | 3.29 | 6.91 | -3.109 | 0.26 | 101
8/10/2025 20:45 | 5 | 19 | 2.75 | 7.857 | 3.712 | 7.17 | 56 | 1.98 | 69.4 | 0.212 | 0.026 | 38.19 | 8839 | 8.36 | 57 |  | 179.09 | 3.28 | 6.84 | -3.109 | 0.27 | 101
8/10/2025 21:00 | 8 | 19 | 2.75 | 7.85 | 4.246 | 7.12 | 56 | 1.98 | 69.4 | 0.212 | 0.026 | 38.19 | 8839 | 8.36 | 57 |  | 178.95 | 3.28 | 6.8 | -3.109 | 0.25 | 101
8/10/2025 21:15 | 10 | 19 | 2.75 | 7.426 | 3.949 | 7.12 | 56 | 1.98 | 69.4 | 0.212 | 0.026 | 38.19 | 8839 | 8.34 | 57 |  | 178.83 | 3.47 | 6.81 | -3.109 | 0.26 | 101
8/10/2025 21:30 | 8 | 19 | 2.75 | 7.476 | 3.524 | 7.13 | 56 | 1.98 | 69.4 | 0.212 | 0.026 | 38.19 | 8839 | 8.33 | 57 |  | 179 | 3.45 | 6.84 | -3.109 | 0.28 | 101
8/10/2025 21:45 | 7 | 19 | 2.75 | 7.865 | 3.156 | 7.15 | 56 | 1.98 | 69.4 | 0.212 | 0.026 | 38.19 | 8839 | 8.33 | 57 |  | 179.03 | 3.28 | 6.87 | -3.109 | 0.28 | 101
8/10/2025 22:00 | 10 | 19 | 2.75 | 8.087 | 3.18 | 7.16 | 58 | 1.98 | 69.2 | 0.212 | 0.026 | 38.19 | 8839 | 8.33 | 57 |  | 178.59 | 3.18 | 6.87 | -3.109 | 0.3 | 101
8/10/2025 22:15 | 9 | 19 | 2.75 | 8.062 | 2.986 | 7.17 | 58 | 1.98 | 69.2 | 0.212 | 0.026 | 37.7 | 8832 | 8.33 | 57 |  | 178.92 | 3.2 | 6.88 | -3.109 | 0.27 | 101
8/10/2025 22:30 | 9 | 19 | 2.75 | 7.541 | 2.724 | 7.18 | 58 | 1.98 | 69.2 | 0.212 | 0.026 | 37.7 | 8832 | 8.34 | 57 |  | 177.98 | 3.4 | 6.9 | -3.109 | 0.31 | 101
8/10/2025 22:45 | 6 | 19 | 2.75 | 7.512 | 2.725 | 7.18 | 58 | 1.98 | 69.2 | 0.212 | 0.026 | 37.7 | 8832 | 8.35 | 57 |  | 178.25 | 3.42 | 6.92 | -3.109 | 0.28 | 101
8/10/2025 23:00 | 10 | 19 | 2.75 | 7.69 | 2.603 | 7.19 | 58 | 1.98 | 69.2 | 0.212 | 0.026 | 37.7 | 8832 | 8.36 | 57 |  | 178.95 | 3.35 | 6.92 | -3.109 | 0.29 | 101
8/10/2025 23:15 | 8 | 19 | 2.75 | 7.975 | 2.421 | 7.2 | 58 | 1.98 | 69.2 | 0.212 | 0.026 | 37.7 | 8832 | 8.35 | 57 |  | 178.86 | 3.23 | 6.91 | -3.109 | 0.27 | 101
8/10/2025 23:30 | 13 | 19 | 2.75 | 7.974 | 2.859 | 7.19 | 58 | 1.98 | 69.2 | 0.212 | 0.026 | 37.7 | 8832 | 8.33 | 57 |  | 178.65 | 3.23 | 6.89 | -3.109 | 0.26 | 101
8/10/2025 23:45 | 6 | 19 | 2.75 | 7.978 | 3.121 | 7.17 | 58 | 1.98 | 69.2 | 0.212 | 0.026 | 37.7 | 8832 | 8.33 | 57 |  | 178.44 | 3.22 | 6.87 | -3.109 | 0.31 | 101
8/11/2025 00:00 | 3 | 19 | 2.75 | 7.321 | 3.395 | 7.16 | 58 | 1.98 | 69.2 | 0.342 | 0.026 | 37.7 | 8832 | 8.36 | 57 |  | 178.67 | 3.51 | 6.86 | -3.109 | 0.25 | 101
8/11/2025 00:15 | 8 | 19 | 2.75 | 7.319 | 3.486 | 7.14 | 58 | 1.98 | 69.2 | 0.342 | 0.026 | 37.7 | 8832 | 8.36 | 57 |  | 178.58 | 3.51 | 6.86 | -3.109 | 0.26 | 101
8/11/2025 00:30 | 6 | 19 | 2.75 | 7.741 | 3.679 | 7.13 | 58 | 1.98 | 69.2 | 0.342 | 0.026 | 37.7 | 8832 | 8.29 | 57 |  | 178.31 | 3.32 | 6.84 | -3.109 | 0.25 | 101
8/11/2025 00:45 | 6 | 19 | 2.75 | 7.711 | 3.546 | 7.13 | 58 | 1.98 | 69.2 | 0.342 | 0.026 | 37.7 | 8832 | 8.21 | 57 |  | 178.31 | 3.33 | 6.83 | -3.109 | 0.26 | 101
8/11/2025 01:00 | 9 | 19 | 2.75 | 7.672 | 4.032 | 7.16 | 58 | 1.98 | 69.2 | 0.342 | 0.026 | 37.7 | 8832 | 8.13 | 57 |  | 0 | 0 | 6.83 | -3.109 | 0.26 | 101
8/11/2025 01:15 | 6 | 19 | 2.75 | 7.665 | 4.002 | 7.17 | 58 | 1.98 | 69.2 | 0.342 | 0.025 | 37.7 | 8832 | 8.12 | 57 |  | 0 | 0 | 6.84 | -3.109 | 0.26 | 101
8/11/2025 01:30 | 2 | 19 | 2.75 | 7.082 | 4.002 | 7.18 | 58 | 1.98 | 69.2 | 0.342 | 0.025 | 37.7 | 8832 | 8.16 | 57 |  | 0 | 0 | 6.87 | -3.109 | 0.29 | 101
8/11/2025 01:45 | 5 | 19 | 2.75 | 7.636 | 4.052 | 7.19 | 58 | 1.98 | 69.2 | 0.342 | 0.025 | 37.7 | 8832 | 8.2 | 57 |  | 180.62 | 3.41 | 6.88 | -3.109 | 0.27 | 101
8/11/2025 02:00 | 5 | 19 | 2.75 | 7.672 | 4.692 | 7.15 | 58 | 1.98 | 69 | 0.342 | 0.025 | 37.7 | 8832 | 8.23 | 57 |  | 181.36 | 3.4 | 6.85 | -3.109 | 0.27 | 101
8/11/2025 02:15 | 6 | 19 | 2.75 | 7.631 | 3.74 | 7.15 | 58 | 1.98 | 69 | 0.342 | 0.025 | 37.7 | 8832 | 8.25 | 57 |  | 181.73 | 3.43 | 6.85 | -3.109 | 0.27 | 101
8/11/2025 02:30 | 7 | 19 | 2.75 | 7.665 | 3.346 | 7.14 | 58 | 1.98 | 69 | 0.342 | 0.025 | 37.7 | 8832 | 8.26 | 57 |  | 181.22 | 3.4 | 6.84 | -3.109 | 0.27 | 101
8/11/2025 02:45 | 5 | 19 | 2.75 | 7.641 | 3.202 | 7.13 | 58 | 1.98 | 69 | 0.342 | 0.025 | 37.7 | 8832 | 8.27 | 57 |  | 181.55 | 3.42 | 6.85 | -3.109 | 0.27 | 101
8/11/2025 03:00 | 9 | 19 | 2.75 | 6.865 | 3.16 | 7.14 | 58 | 1.98 | 69 | 0.342 | 0.025 | 37.7 | 8832 | 8.27 | 57 |  | 167.34 | 3.51 | 6.86 | -3.109 | 0.26 | 101
8/11/2025 03:15 | 13 | 19 | 2.75 | 6.894 | 3.39 | 7.13 | 58 | 1.98 | 69 | 0.342 | 0.025 | 37.7 | 8832 | 8.27 | 57 |  | 167.14 | 3.49 | 6.88 | -3.109 | 0.26 | 101
8/11/2025 03:30 | 9 | 19 | 2.75 | 7.508 | 3.188 | 7.13 | 58 | 1.98 | 69 | 0.342 | 0.025 | 37.7 | 8832 | 8.27 | 57 |  | 180.88 | 3.47 | 6.86 | -3.109 | 0.24 | 101
8/11/2025 03:45 | 6 | 19 | 2.75 | 7.48 | 3.203 | 7.14 | 58 | 1.98 | 69 | 0.342 | 0.025 | 37.7 | 8832 | 8.27 | 57 |  | 181.06 | 3.49 | 6.86 | -3.109 | 0.25 | 101
8/11/2025 04:00 | 7 | 19 | 2.75 | 7.502 | 3.174 | 7.15 | 58 | 1.98 | 69 | 0.339 | 0.025 | 37.7 | 8832 | 8.27 | 57 |  | 180.98 | 3.47 | 6.86 | -3.109 | 0.27 | 101
8/11/2025 04:15 | 5 | 19 | 2.75 | 7.528 | 3.21 | 7.16 | 58 | 1.98 | 69 | 0.339 | 0.025 | 37.7 | 8832 | 8.26 | 57 |  | 180.65 | 3.46 | 6.86 | -3.109 | 0.26 | 101
8/11/2025 04:30 | 5 | 19 | 2.75 | 7.282 | 3.092 | 7.16 | 58 | 1.98 | 69 | 0.339 | 0.025 | 37.7 | 8832 | 8.26 | 57 |  | 177.45 | 3.51 | 6.87 | -3.109 | 0.24 | 101
8/11/2025 04:45 | 5 | 19 | 2.75 | 7.046 | 3.467 | 7.15 | 58 | 1.98 | 69 | 0.339 | 0.025 | 37.7 | 8832 | 8.26 | 57 |  | 171.42 | 3.5 | 6.88 | -3.109 | 0.23 | 101
8/11/2025 05:00 | 4 | 19 | 2.75 | 7.223 | 3.583 | 7.12 | 58 | 1.98 | 69 | 0.339 | 0.025 | 37.7 | 8832 | 8.25 | 57 |  | 175.43 | 3.5 | 6.85 | -3.109 | 0.24 | 101
8/11/2025 05:15 | 3 | 19 | 2.75 | 7.465 | 3.579 | 7.12 | 58 | 1.98 | 69 | 0.339 | 0.025 | 37.7 | 8832 | 8.24 | 57 |  | 180.04 | 3.47 | 6.83 | -3.109 | 0.24 | 101
8/11/2025 05:30 | 5 | 19 | 2.75 | 7.487 | 3.742 | 7.11 | 58 | 1.98 | 69 | 0.339 | 0.025 | 37.7 | 8832 | 8.24 | 57 |  | 180.28 | 3.47 | 6.83 | -3.109 | 0.24 | 101
8/11/2025 05:45 | 6 | 19 | 2.75 | 7.784 | 3.557 | 7.12 | 58 | 1.98 | 69 | 0.339 | 0.025 | 37.7 | 8832 | 8.24 | 57 |  | 180.08 | 3.33 | 6.82 | -3.109 | 0.25 | 101
8/11/2025 06:00 | 2 | 19 | 2.75 | 7.766 | 3.475 | 7.12 | 58 | 1.98 | 68.9 | 0.339 | 0.025 | 37.7 | 8832 | 8.24 | 57 |  | 180.19 | 3.34 | 6.83 | -3.109 | 0.25 | 101
8/11/2025 06:15 | 1 | 19 | 2.75 | 7.914 | 3.378 | 7.13 | 58 | 1.98 | 68.9 | 0.339 | 0.025 | 37.7 | 8832 | 8.24 | 57 |  | 179.9 | 3.27 | 6.83 | -3.109 | 0.26 | 101
8/11/2025 06:30 | 4 | 19 | 2.75 | 7.911 | 3.255 | 7.13 | 58 | 1.98 | 68.9 | 0.339 | 0.025 | 37.7 | 8832 | 8.23 | 57 |  | 179.55 | 3.27 | 6.83 | -3.109 | 0.25 | 101
8/11/2025 06:45 | 5 | 19 | 2.75 | 7.854 | 3.21 | 7.13 | 58 | 1.98 | 68.9 | 0.339 | 0.025 | 37.7 | 8832 | 8.22 | 57 |  | 179.69 | 3.29 | 6.84 | -3.109 | 0.25 | 101
8/11/2025 07:00 | 9 | 19 | 2.75 | 7.9 | 3.159 | 7.14 | 58 | 1.98 | 68.9 | 0.339 | 0.025 | 37.7 | 8832 | 8.22 | 57 |  | 179.83 | 3.28 | 6.85 | -3.109 | 0.27 | 101
8/11/2025 07:15 | 7 | 19 | 2.75 | 7.915 | 3.081 | 7.14 | 58 | 1.98 | 68.9 | 0.339 | 0.025 | 37.7 | 8832 | 8.21 | 57 |  | 179.86 | 3.27 | 6.85 | -3.109 | 0.25 | 101
8/11/2025 07:30 | 7 | 19 | 2.75 | 7.9 | 3.059 | 7.14 | 58 | 1.98 | 68.9 | 0.339 | 0.024 | 37.7 | 8832 | 8.21 | 57 |  | 179.96 | 3.28 | 6.85 | -3.109 | 0.25 | 101
8/11/2025 07:45 | 5 | 19 | 2.75 | 7.897 | 3.149 | 7.13 | 58 | 1.98 | 68.9 | 0.339 | 0.024 | 37.7 | 8832 | 8.21 | 57 |  | 180.28 | 3.29 | 6.84 | -3.109 | 0.26 | 101
8/11/2025 08:00 | 6 | 19 | 2.75 | 7.927 | 3.185 | 7.13 | 58 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.21 | 57 |  | 179.96 | 3.27 | 6.85 | -3.109 | 0.25 | 101
8/11/2025 08:15 | 7 | 19 | 2.75 | 7.886 | 3.322 | 7.13 | 58 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.21 | 57 |  | 179.62 | 3.28 | 6.85 | -3.109 | 0.35 | 101
8/11/2025 08:30 | 2 | 19 | 2.75 | 7.888 | 3.33 | 7.13 | 58 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.21 | 57 |  | 179.74 | 3.28 | 6.78 | -3.109 | 0.22 | 101
8/11/2025 08:45 | 6 | 19 | 2.75 | 7.921 | 3.283 | 7.14 | 58 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.21 | 57 |  | 179.39 | 3.26 | 6.78 | -3.109 | 0.24 | 101
8/11/2025 09:00 | 10 | 19 | 2.75 | 7.33 | 3.215 | 7.14 | 58 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.21 | 57 |  | 0 | 0 | 6.85 | -3.109 | 0.25 | 101
8/11/2025 09:15 | 10 | 19 | 2.75 | 7.051 | 3.714 | 7.18 | 58 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.2 | 57 |  | 0 | 0 | 6.88 | -3.109 | 0.25 | 101
8/11/2025 09:30 | -7 | 19 | 2.75 | 6.981 | 3.655 | 7.19 | 58 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.2 | 57 |  | 0 | 0 | 6.88 | -3.109 | 0.33 | 101
8/11/2025 09:45 | 3 | 19 | 2.75 | 7.361 | 3.782 | 7.2 | 58 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.2 | 57 |  | 0 | 0 | 6.87 | -3.109 | 0.26 | 101
8/11/2025 10:00 | 5 | 19 | 2.75 | 7.397 | 3.855 | 7.21 | 56 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.21 | 57 |  | 0 | 0 | 6.87 | -3.109 | 0.27 | 101
8/11/2025 10:15 | 4 | 19 | 2.75 | 7.411 | 4.475 | 7.2 | 56 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.22 | 57 |  | 179.38 | 3.49 | 6.85 | -3.109 | 0.25 | 101
8/11/2025 10:30 | 6 | 19 | 2.75 | 7.398 | 2.755 | 7.1 | 56 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.22 | 57 |  | 179.66 | 3.5 | 6.86 | -3.109 | 0.26 | 101
8/11/2025 10:45 | 5 | 19 | 2.75 | 7.374 | 2.57 | 7.14 | 56 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.22 | 57 |  | 178.31 | 3.48 | 6.86 | -3.109 | 0.29 | 101
8/11/2025 11:00 | 9 | 19 | 2.75 | 7.364 | 2.266 | 7.15 | 56 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.22 | 57 |  | 179.41 | 3.51 | 6.86 | -3.109 | 0.26 | 101
8/11/2025 11:15 | 7 | 19 | 2.75 | 7.381 | 2.333 | 7.19 | 56 | 1.98 | 68.9 | 0.35 | 0.023 | 37.7 | 8832 | 8.22 | 57 |  | 76.87 | 1.5 | 6.87 | -3.109 | 0.26 | 101
8/11/2025 11:30 | 8 | 19 | 2.75 | 7.348 | 2.172 | 7.2 | 56 | 1.98 | 68.9 | 0.35 | 0.024 | 37.7 | 8832 | 8.23 | 57 |  | 76.98 | 1.51 | 6.87 | -3.109 | 0.28 | 101
8/11/2025 11:45 | 7 | 19 | 2.75 | 7.386 | 2.207 | 7.21 | 56 | 1.98 | 68.9 | 0.35 | 0.023 | 37.7 | 8832 | 8.23 | 57 |  | 77.13 | 1.5 | 6.87 | -3.109 | 0.28 | 101
8/11/2025 12:00 | 8 | 19 | 2.75 | 7.377 | 2.143 | 7.21 | 56 | 1.98 | 68.9 | 0.239 | 0.023 | 37.7 | 8832 | 8.23 | 57 |  | 77.06 | 1.5 | 6.87 | -3.1 | 0.27 | 101
8/11/2025 12:15 | 8 | 19 | 2.75 | 6.866 | 2.169 | 7.22 | 56 | 1.98 | 68.9 | 0.239 | 0.023 | 37.7 | 8832 | 8.24 | 57 |  | 72.13 | 1.51 | 6.88 | -3.1 | 0.27 | 101
8/11/2025 12:30 | 7 | 19 | 2.75 | 6.759 | 2.3 | 7.21 | 56 | 1.98 | 68.9 | 0.239 | 0.023 | 37.7 | 8832 | 8.24 | 57 |  | 70.73 | 1.51 | 6.88 | -3.1 | 0.26 | 101
8/11/2025 12:45 | 9 | 19 | 2.75 | 7.102 | 2.713 | 7.2 | 56 | 1.98 | 68.9 | 0.239 | 0.023 | 37.7 | 8832 | 8.24 | 57 |  | 74.14 | 1.5 | 6.86 | -3.1 | 0.25 | 101
8/11/2025 13:00 | 9 | 19 | 2.75 | 7.107 | 2.757 | 7.19 | 56 | 1.98 | 68.9 | 0.239 | 0.023 | 37.7 | 8832 | 8.25 | 57 |  | 74.15 | 1.5 | 6.75 | -3.1 | 0.26 | 101
8/11/2025 13:15 | -10 | 19 | 2.75 | 7.106 | 2.804 | 7.19 | 56 | 1.98 | 68.9 | 0.239 | 0.023 | 37.7 | 8832 | 8.25 | 57 |  | 73.95 | 1.5 | 6.9 | -3.1 | 0.27 | 101
8/11/2025 13:30 | -13 | 19 | 2.75 | 7.101 | 2.763 | 7.2 | 56 | 1.98 | 68.9 | 0.239 | 0.023 | 37.7 | 8832 | 8.25 | 57 |  | 74.29 | 1.51 | 6.87 | -3.1 | 0.27 | 100
8/11/2025 13:45 | 1 | 19 | 2.75 | 6.651 | 2.67 | 7.21 | 56 | 1.98 | 68.9 | 0.239 | 0.023 | 37.7 | 8832 | 8.25 | 57 |  | 69.72 | 1.51 | 6.87 | -3.1 | 0.15 | 101
8/11/2025 14:00 | 7 | 19 | 2.75 | 6.511 | 2.768 | 7.2 | 56 | 1.98 | 69 | 0.239 | 0.023 | 37.7 | 8832 | 8.25 | 59 |  | 68.47 | 1.51 | 6.87 | -3.1 | 0.2 | 101
8/11/2025 14:15 | 7 | 19 | 2.75 | 6.945 | 2.764 | 7.2 | 56 | 1.98 | 69 | 0.239 | 0.023 | 37.7 | 8832 | 8.25 | 59 |  | 72.54 | 1.5 | 6.86 | -3.1 | 0.27 | 101
8/11/2025 14:30 | 7 | 19 | 2.75 | 7.013 | 2.626 | 7.21 | 56 | 1.98 | 69 | 0.239 | 0.023 | 37.7 | 8832 | 8.25 | 59 |  | 72.2 | 1.48 | 6.86 | -3.1 | 0.26 | 101
8/11/2025 14:45 | 6 | 19 | 2.75 | 6.987 | 2.842 | 7.21 | 56 | 1.98 | 69 | 0.239 | 0.023 | 37.7 | 8832 | 8.23 | 59 |  | 72.53 | 1.49 | 6.87 | -3.1 | 0.25 | 101
8/11/2025 15:00 | 7 | 19 | 2.75 | 6.974 | 2.961 | 7.19 | 56 | 1.98 | 69 | 0.239 | 0.022 | 37.7 | 8832 | 8.08 | 59 |  | 72.38 | 1.49 | 6.85 | -3.1 | 0.25 | 101
8/11/2025 15:15 | 9 | 19 | 2.75 | 6.338 | 3.393 | 7.16 | 56 | 1.98 | 69 | 0.239 | 0.022 | 37.7 | 8832 | 7.87 | 59 |  | 65.96 | 1.5 | 6.83 | -3.1 | 0.25 | 101
8/11/2025 15:30 | 8 | 19 | 2.75 | 6.661 | 3.559 | 7.14 | 56 | 1.98 | 69 | 0.239 | 0.022 | 37.7 | 8832 | 7.77 | 59 |  | 69.27 | 1.5 | 6.84 | -3.1 | 0.24 | 101
8/11/2025 15:45 | 8 | 19 | 2.75 | 6.703 | 3.628 | 7.15 | 56 | 1.98 | 69 | 0.239 | 0.022 | 37.7 | 8832 | 7.83 | 59 |  | 69.18 | 1.49 | 6.83 | -3.1 | 0.25 | 101
8/11/2025 16:00 | 9 | 19 | 2.75 | 6.682 | 3.595 | 7.15 | 56 | 1.98 | 69 | 0.2 | 0.022 | 37.7 | 8832 | 7.96 | 59 |  | 69.26 | 1.49 | 6.83 | -3.1 | 0.26 | 101
8/11/2025 16:15 | 11 | 19 | 2.75 | 6.663 | 3.404 | 7.19 | 56 | 1.98 | 69 | 0.2 | 0.022 | 37.7 | 8832 | 8.07 | 59 |  | 46.72 | 1.01 | 6.84 | -3.1 | 0.26 | 101
8/11/2025 16:30 | 11 | 19 | 2.75 | 6.7 | 3.392 | 7.19 | 56 | 1.98 | 69 | 0.2 | 0.022 | 37.7 | 8832 | 8.14 | 59 |  | 46.57 | 1 | 6.85 | -3.1 | 0.25 | 101
8/11/2025 16:45 | 12 | 19 | 2.75 | 6.686 | 3.343 | 7.2 | 56 | 1.98 | 69 | 0.2 | 0.022 | 37.7 | 8832 | 8.18 | 59 |  | 46.67 | 1.01 | 6.84 | -3.1 | 0.27 | 101
8/11/2025 17:00 | 12 | 19 | 2.75 | 6.656 | 3.276 | 7.21 | 56 | 1.98 | 69 | 0.2 | 0.022 | 37.7 | 8832 | 8.21 | 59 |  | 46.35 | 1 | 6.85 | -3.1 | 0.26 | 101
8/11/2025 17:15 | 10 | 19 | 2.75 | 6.697 | 3.41 | 7.23 | 56 | 1.98 | 69 | 0.2 | 0.022 | 37.7 | 8832 | 8.22 | 59 |  | 46.44 | 1 | 6.87 | -3.1 | 0.27 | 101
8/11/2025 17:30 | 9 | 19 | 2.75 | 6.71 | 3.559 | 7.23 | 56 | 1.98 | 69 | 0.2 | 0.022 | 37.7 | 8832 | 8.24 | 59 |  | 46.4 | 1 | 6.87 | -3.1 | 0.26 | 101
8/11/2025 17:45 | 8 | 19 | 2.75 | 6.658 | 3.559 | 7.22 | 56 | 1.98 | 69 | 0.2 | 0.022 | 37.7 | 8832 | 8.25 | 59 |  | 46.66 | 1.01 | 6.86 | -3.1 | 0.28 | 101
8/11/2025 18:00 | 11 | 19 | 2.75 | 6.71 | 3.949 | 7.19 | 56 | 1.98 | 69.2 | 0.2 | 0.022 | 37.7 | 8832 | 8.25 | 59 |  | 46.21 | 0.99 | 6.84 | -3.1 | 0.27 | 101
8/11/2025 18:15 | 11 | 19 | 2.75 | 6.768 | 3.964 | 7.19 | 56 | 1.98 | 69.2 | 0.2 | 0.022 | 37.7 | 8832 | 8.26 | 59 |  | 46.62 | 0.99 | 6.83 | -3.1 | 0.26 | 101
8/11/2025 18:30 | 11 | 19 | 2.75 | 6.705 | 3.685 | 7.19 | 56 | 1.98 | 69.2 | 0.2 | 0.022 | 37.7 | 8832 | 8.26 | 59 |  | 46.32 | 0.99 | 6.84 | -3.1 | 0.28 | 101
8/11/2025 18:45 | 9 | 19 | 2.75 | 6.711 | 3.462 | 7.22 | 56 | 1.98 | 69.2 | 0.2 | 0.022 | 37.7 | 8832 | 8.26 | 59 |  | 46.62 | 1 | 6.85 | -3.1 | 0.27 | 101
8/11/2025 19:00 | 9 | 19 | 2.75 | 6.683 | 3.694 | 7.23 | 56 | 1.98 | 69.2 | 0.2 | 0.022 | 37.7 | 8832 | 8.27 | 59 |  | 46.16 | 0.99 | 6.86 | -3.1 | 0.27 | 101
8/11/2025 19:15 | 10 | 19 | 2.75 | 6.5 | 3.629 | 7.22 | 56 | 1.98 | 69.2 | 0.2 | 0.022 | 37.7 | 8832 | 8.27 | 59 |  | 46.06 | 1.02 | 6.86 | -3.1 | 0.26 | 101
8/11/2025 19:30 | 11 | 19 | 2.75 | 6.353 | 3.634 | 7.21 | 56 | 1.98 | 69.2 | 0.2 | 0.023 | 37.7 | 8832 | 8.27 | 59 |  | 44.54 | 1.01 | 6.85 | -3.1 | 0.29 | 101
8/11/2025 19:45 | 11 | 19 | 2.75 | 6.636 | 3.449 | 7.22 | 56 | 1.98 | 69.2 | 0.2 | 0.023 | 37.7 | 8832 | 8.28 | 59 |  | 45.77 | 0.99 | 6.86 | -3.1 | 0.27 | 101
8/11/2025 20:00 | 11 | 19 | 2.75 | 7.194 | 3.928 | 7.18 | 56 | 1.98 | 69.2 | 0.197 | 0.022 | 37.7 | 8832 | 8.28 | 59 |  | 148.8 | 2.98 | 6.83 | -3.1 | 0.26 | 101
8/11/2025 20:15 | 11 | 19 | 2.75 | 7.15 | 3.576 | 7.15 | 56 | 1.98 | 69.2 | 0.197 | 0.023 | 37.64 | 8777 | 8.28 | 59 |  | 149.45 | 3.01 | 6.81 | -3.1 | 0.33 | 101
8/11/2025 20:30 | 10 | 19 | 2.75 | 7.14 | 3.473 | 7.14 | 56 | 1.98 | 69.2 | 0.197 | 0.024 | 37.64 | 8777 | 8.28 | 59 |  | 148.56 | 3 | 6.79 | -3.1 | 0.27 | 101
8/11/2025 20:45 | 11 | 19 | 2.75 | 7.177 | 3.198 | 7.15 | 56 | 1.98 | 69.2 | 0.197 | 0.025 | 37.64 | 8777 | 8.28 | 59 |  | 149.1 | 2.99 | 6.8 | -3.1 | 0.27 | 101
8/11/2025 21:00 | 11 | 19 | 2.75 | 6.997 | 3.084 | 7.15 | 56 | 1.98 | 69.2 | 0.197 | 0.025 | 37.64 | 8777 | 8.28 | 59 |  | 146.15 | 3.01 | 6.81 | -3.1 | 0.27 | 101
8/11/2025 21:15 | 13 | 19 | 2.75 | 6.75 | 2.935 | 7.15 | 56 | 1.98 | 69.2 | 0.197 | 0.025 | 37.64 | 8777 | 8.27 | 59 |  | 140.68 | 3 | 6.82 | -3.1 | 0.26 | 101
8/11/2025 21:30 | 13 | 19 | 2.75 | 7.017 | 2.93 | 7.16 | 56 | 1.98 | 69.2 | 0.197 | 0.025 | 37.64 | 8777 | 8.25 | 59 |  | 146.48 | 3.01 | 6.84 | -3.1 | 0.26 | 101
8/11/2025 21:45 | 13 | 19 | 2.75 | 6.977 | 2.801 | 7.17 | 56 | 1.98 | 69.2 | 0.197 | 0.025 | 37.64 | 8777 | 8.24 | 59 |  | 145.26 | 3 | 6.83 | -3.1 | 0.28 | 101
8/11/2025 22:00 | 13 | 19 | 2.75 | 7.481 | 2.864 | 7.16 | 58 | 1.98 | 69.2 | 0.197 | 0.025 | 37.64 | 8777 | 8.26 | 59 |  | 179.41 | 3.45 | 6.82 | -3.1 | 0.26 | 101
8/11/2025 22:15 | 13 | 19 | 2.75 | 7.48 | 2.611 | 7.16 | 58 | 1.98 | 69.2 | 0.197 | 0.024 | 38.4 | 8835 | 8.28 | 59 |  | 179.31 | 3.45 | 6.81 | -3.1 | 0.26 | 101
8/11/2025 22:30 | 13 | 19 | 2.75 | 7.497 | 2.692 | 7.16 | 58 | 1.98 | 69.2 | 0.197 | 0.026 | 38.4 | 8835 | 8.29 | 59 |  | 179.78 | 3.45 | 6.81 | -3.1 | 0.27 | 101
8/11/2025 22:45 | 14 | 19 | 2.75 | 7.474 | 2.851 | 7.15 | 58 | 1.98 | 69.2 | 0.197 | 0.026 | 38.4 | 8835 | 8.28 | 59 |  | 178.9 | 3.45 | 6.81 | -3.1 | 0.27 | 101
8/11/2025 23:00 | 14 | 19 | 2.75 | 7.499 | 2.954 | 7.14 | 58 | 1.98 | 69.2 | 0.197 | 0.026 | 38.4 | 8835 | 8.27 | 59 |  | 179.36 | 3.44 | 6.81 | -3.1 | 0.27 | 101
8/11/2025 23:15 | 14 | 19 | 2.75 | 7.452 | 2.952 | 7.13 | 58 | 1.98 | 69.2 | 0.197 | 0.026 | 38.4 | 8835 | 8.25 | 59 |  | 178.73 | 3.45 | 6.8 | -3.1 | 0.27 | 100
8/11/2025 23:30 | 13 | 19 | 2.75 | 7.426 | 2.976 | 7.13 | 58 | 1.98 | 69.2 | 0.197 | 0.025 | 38.4 | 8835 | 8.21 | 59 |  | 0 | 0 | 6.8 | -3.1 | 0.28 | 101
8/11/2025 23:45 | 12 | 19 | 2.75 | 7.428 | 3.418 | 7.17 | 58 | 1.98 | 69.2 | 0.197 | 0.025 | 38.4 | 8835 | 8.18 | 59 |  | 0 | 0 | 6.81 | -3.1 | 0.27 | 101
8/12/2025 00:00 | 12 | 19 | 2.75 | 7.389 | 3.038 | 7.15 | 58 | 1.98 | 69.2 | 0.392 | 0.025 | 38.4 | 8835 | 8.19 | 59 |  | 180.37 | 3.52 | 6.83 | -3.1 | 0.27 | 101
8/12/2025 00:15 | 12 | 19 | 2.75 | 7.418 | 3.516 | 7.14 | 58 | 1.98 | 69.2 | 0.392 | 0.025 | 38.4 | 8835 | 8.2 | 59 |  | 180.74 | 3.51 | 6.84 | -3.1 | 0.28 | 101
8/12/2025 00:30 | 13 | 19 | 2.75 | 7.516 | 2.866 | 7.14 | 58 | 1.98 | 69.2 | 0.392 | 0.025 | 38.4 | 8835 | 8.21 | 59 |  | 180.9 | 3.47 | 6.84 | -3.1 | 0.29 | 101
8/12/2025 00:45 | 10 | 19 | 2.75 | 7.423 | 2.84 | 7.13 | 58 | 1.98 | 69.2 | 0.392 | 0.025 | 38.4 | 8835 | 8.21 | 59 |  | 180.63 | 3.5 | 6.84 | -3.1 | 0.27 | 101
8/12/2025 01:00 | 5 | 19 | 2.75 | 7.423 | 3.054 | 7.12 | 58 | 1.98 | 69.2 | 0.392 | 0.025 | 38.4 | 8835 | 8.2 | 59 |  | 180.3 | 3.5 | 6.82 | -3.1 | 0.26 | 101
8/12/2025 01:15 | 12 | 19 | 2.75 | 7.432 | 3.004 | 7.11 | 58 | 1.98 | 69.2 | 0.392 | 0.024 | 38.4 | 8835 | 8.19 | 59 |  | 180.41 | 3.5 | 6.84 | -3.1 | 0.26 | 101
8/12/2025 01:30 | 10 | 19 | 2.75 | 7.406 | 3.024 | 7.11 | 58 | 1.98 | 69.2 | 0.392 | 0.024 | 38.4 | 8835 | 8.18 | 59 |  | 180.11 | 3.5 | 6.83 | -3.1 | 0.26 | 101
8/12/2025 01:45 | 12 | 19 | 2.75 | 7.414 | 3.009 | 7.1 | 58 | 1.98 | 69.2 | 0.392 | 0.024 | 38.4 | 8835 | 8.17 | 59 |  | 180.73 | 3.51 | 6.83 | -3.1 | 0.25 | 101
8/12/2025 02:00 | 12 | 19 | 2.75 | 7.434 | 3.144 | 7.1 | 58 | 1.98 | 69.2 | 0.392 | 0.024 | 38.4 | 8835 | 8.17 | 58 |  | 180.85 | 3.5 | 6.83 | -3.1 | 0.26 | 101
8/12/2025 02:15 | 12 | 19 | 2.75 | 7.375 | 3.181 | 7.09 | 58 | 1.98 | 69.2 | 0.392 | 0.024 | 38.4 | 8835 | 8.17 | 58 |  | 179.99 | 3.51 | 6.82 | -3.1 | 0.28 | 101
8/12/2025 02:30 | 13 | 19 | 2.75 | 7.229 | 3.091 | 7.08 | 58 | 1.98 | 69.2 | 0.392 | 0.024 | 37.57 | 8710 | 8.16 | 58 |  | 176.58 | 3.52 | 6.8 | -3.1 | 0.26 | 101
8/12/2025 02:45 | 12 | 19 | 2.75 | 6.956 | 3.155 | 7.08 | 58 | 1.98 | 69.2 | 0.392 | 0.025 | 37.57 | 8710 | 8.16 | 58 |  | 169.36 | 3.51 | 6.82 | -3.1 | 0.28 | 101
8/12/2025 03:00 | 12 | 19 | 2.75 | 6.978 | 3.046 | 7.09 | 58 | 1.98 | 69.2 | 0.392 | 0.026 | 37.57 | 8710 | 8.16 | 58 |  | 168.59 | 3.48 | 6.82 | -3.1 | 0.26 | 101
8/12/2025 03:15 | 12 | 19 | 2.75 | 7.009 | 2.958 | 7.09 | 58 | 1.98 | 69.2 | 0.392 | 0.026 | 37.57 | 8710 | 8.16 | 58 |  | 170.43 | 3.5 | 6.82 | -3.1 | 0.3 | 101
8/12/2025 03:30 | 12 | 19 | 2.75 | 7.186 | 3.016 | 7.09 | 58 | 1.98 | 69.2 | 0.392 | 0.025 | 37.57 | 8710 | 8.16 | 58 |  | 174.77 | 3.5 | 6.81 | -3.1 | 0.27 | 101
8/12/2025 03:45 | 12 | 19 | 2.75 | 7.182 | 2.939 | 7.09 | 58 | 1.98 | 69.2 | 0.392 | 0.025 | 37.57 | 8710 | 8.16 | 58 |  | 174.39 | 3.5 | 6.81 | -3.1 | 0.26 | 101
8/12/2025 04:00 | 12 | 19 | 2.75 | 7.187 | 3.055 | 7.08 | 58 | 1.98 | 69.2 | 0.363 | 0.025 | 37.57 | 8710 | 8.17 | 58 |  | 173.88 | 3.48 | 6.8 | -3.1 | 0.25 | 101
8/12/2025 04:15 | 11 | 19 | 2.75 | 7.179 | 3.075 | 7.08 | 58 | 1.98 | 69.2 | 0.363 | 0.025 | 37.57 | 8710 | 8.19 | 58 |  | 174.68 | 3.5 | 6.8 | -3.1 | 0.28 | 101
8/12/2025 04:30 | 10 | 19 | 2.75 | 7.205 | 3.087 | 7.08 | 58 | 1.98 | 69.2 | 0.363 | 0.025 | 37.57 | 8710 | 8.23 | 58 |  | 174.42 | 3.49 | 6.8 | -3.1 | 0.26 | 101
8/12/2025 04:45 | 10 | 19 | 2.75 | 7.186 | 3.21 | 7.08 | 58 | 1.98 | 69.2 | 0.363 | 0.025 | 37.57 | 8710 | 8.24 | 58 |  | 174.31 | 3.49 | 6.79 | -3.1 | 0.25 | 101
8/12/2025 05:00 | 10 | 19 | 2.75 | 7.224 | 3.249 | 7.08 | 58 | 1.98 | 69.2 | 0.363 | 0.025 | 37.57 | 8710 | 8.24 | 58 |  | 175.11 | 3.49 | 6.8 | -3.1 | 0.25 | 101
8/12/2025 05:15 | 10 | 19 | 2.75 | 7.16 | 3.317 | 7.08 | 58 | 1.98 | 69.2 | 0.363 | 0.024 | 37.57 | 8710 | 8.23 | 58 |  | 174.89 | 3.52 | 6.8 | -3.1 | 0.25 | 101
8/12/2025 05:30 | 11 | 19 | 2.75 | 7.213 | 3.258 | 7.07 | 58 | 1.98 | 69.2 | 0.363 | 0.024 | 37.57 | 8710 | 8.22 | 58 |  | 174.83 | 3.49 | 6.79 | -3.1 | 0.27 | 101
8/12/2025 05:45 | 11 | 19 | 2.75 | 7.18 | 3.619 | 7.1 | 58 | 1.98 | 69.2 | 0.363 | 0.024 | 37.57 | 8710 | 8.2 | 58 |  | 0 | 0 | 6.8 | -3.1 | 0.25 | 101
8/12/2025 06:00 | 10 | 19 | 2.75 | 7.17 | 3.725 | 7.12 | 58 | 1.98 | 69 | 0.363 | 0.024 | 37.57 | 8710 | 8.19 | 58 |  | 0 | 0 | 6.8 | -3.1 | 0.26 | 101
8/12/2025 06:15 | 9 | 19 | 2.75 | 7.216 | 4.072 | 7.12 | 58 | 1.98 | 69 | 0.363 | 0.024 | 37.57 | 8710 | 8.18 | 58 |  | 0 | 0 | 6.8 | -3.1 | 0.26 | 101
8/12/2025 06:30 | 10 | 19 | 2.75 | 7.183 | 4.348 | 7.11 | 58 | 1.98 | 69 | 0.363 | 0.024 | 37.57 | 8710 | 8.17 | 58 |  | 0 | 0 | 6.79 | -3.1 | 0.36 | 101
8/12/2025 06:45 | 9 | 19 | 2.75 | 7.168 | 4.6 | 7.11 | 58 | 1.98 | 69 | 0.363 | 0.024 | 37.57 | 8710 | 8.16 | 58 |  | 0 | 0 | 6.79 | -3.1 | 0.23 | 101
8/12/2025 07:00 | 10 | 19 | 2.75 | 7.211 | 4.688 | 7.12 | 58 | 1.98 | 69 | 0.363 | 0.024 | 37.57 | 8710 | 8.15 | 58 |  | 0 | 0 | 6.81 | -3.1 | 0.25 | 101
8/12/2025 07:15 | 9 | 19 | 2.75 | 7.571 | 4.627 | 7.13 | 58 | 1.98 | 69 | 0.363 | 0.024 | 37.57 | 8710 | 8.15 | 58 |  | 0 | 0 | 6.81 | -3.1 | 0.26 | 101
8/12/2025 07:30 | 10 | 19 | 2.75 | 7.882 | 4.511 | 7.14 | 58 | 1.98 | 69 | 0.363 | 0.024 | 37.57 | 8710 | 8.13 | 58 |  | 0 | 0 | 6.81 | -3.1 | 0.27 | 101
8/12/2025 07:45 | 6 | 19 | 2.75 | 7.878 | 4.496 | 7.15 | 58 | 1.98 | 69 | 0.363 | 0.025 | 37.84 | 8707 | 8.13 | 58 |  | 0 | 0 | 6.81 | -3.1 | 0.26 | 101
8/12/2025 08:00 | 9 | 19 | 2.75 | 7.866 | 4.471 | 7.15 | 58 | 1.98 | 69 | 0.293 | 0.025 | 37.84 | 8707 | 8.12 | 58 |  | 0 | 0 | 6.81 | -3.1 | 0.25 | 101
8/12/2025 08:15 | 8 | 19 | 2.75 | 7.904 | 4.401 | 7.16 | 58 | 1.98 | 69 | 0.293 | 0.025 | 37.84 | 8707 | 8.11 | 58 |  | 0 | 0 | 6.81 | -3.1 | 0.25 | 101
8/12/2025 08:30 | 10 | 19 | 2.75 | 7.861 | 4.328 | 7.18 | 58 | 1.98 | 69 | 0.293 | 0.025 | 37.84 | 8707 | 8.1 | 58 |  | 0 | 0 | 6.79 | -3.1 | 0.25 | 101
8/12/2025 08:45 | 8 | 19 | 2.75 | 7.87 | 3.643 | 7.11 | 58 | 1.98 | 69 | 0.293 | 0.025 | 37.84 | 8707 | 8.07 | 58 |  | 0 | 0 | 6.76 | -3.1 | 0.24 | 101
8/12/2025 09:00 | 8 | 19 | 2.75 | 7.856 | 3.777 | 7.13 | 58 | 1.98 | 69 | 0.293 | 0.025 | 37.84 | 8707 | 8.06 | 58 |  | 0 | 0 | 6.74 | -3.1 | 0.26 | 101
8/12/2025 09:15 | 11 | 19 | 2.75 | 7.833 | 3.574 | 7.16 | 58 | 1.98 | 69 | 0.293 | 0.025 | 37.84 | 8707 | 8.09 | 58 |  | 0 | 0 | 6.78 | -3.1 | 0.26 | 101
8/12/2025 09:30 | 9 | 19 | 2.75 | 7.85 | 3.531 | 7.17 | 58 | 1.98 | 69 | 0.293 | 0.025 | 37.84 | 8707 | 8.12 | 58 |  | 0 | 0 | 6.82 | -3.1 | 0.26 | 101
8/12/2025 09:45 | 1 | 19 | 2.75 | 7.851 | 3.588 | 7.17 | 58 | 1.98 | 69 | 0.293 | 0.025 | 37.84 | 8707 | 8.14 | 58 |  | 131.76 | 2.42 | 6.82 | -3.1 | 0.26 | 101
8/12/2025 10:00 | 4 | 19 | 2.75 | 7.843 | 9.871 | 7.12 | 53 | 1.98 | 69 | 0.293 | 0.025 | 37.84 | 8707 | 8.14 | 58 |  | 136.47 | 2.51 | 6.82 | -3.1 | 0.27 | 101
8/12/2025 10:15 | 3 | 19 | 2.75 | 7.672 | 3.345 | 7.14 | 53 | 1.98 | 69 | 0.293 | 0.024 | 37.84 | 8707 | 8.13 | 58 |  | 133.72 | 2.51 | 6.83 | -3.1 | 0.26 | 101
8/12/2025 10:30 | 3 | 19 | 2.75 | 7.719 | 3.038 | 7.13 | 53 | 1.98 | 69 | 0.293 | 0.024 | 37.84 | 8707 | 8.13 | 58 |  | 133.36 | 2.49 | 6.83 | -3.1 | 0.25 | 101
8/12/2025 10:45 | 5 | 19 | 2.75 | 7.699 | 2.731 | 7.14 | 53 | 1.98 | 69 | 0.293 | 0.024 | 37.84 | 8707 | 8.12 | 58 |  | 133.52 | 2.5 | 6.85 | -3.1 | 0.27 | 101
8/12/2025 11:00 | 3 | 19 | 2.75 | 7.706 | 2.663 | 7.15 | 53 | 1.98 | 69 | 0.293 | 0.024 | 37.84 | 8707 | 8.11 | 58 |  | 133.76 | 2.5 | 6.86 | -3.1 | 0.25 | 101
8/12/2025 11:15 | 5 | 19 | 2.75 | 7.711 | 2.68 | 7.14 | 53 | 1.98 | 69 | 0.293 | 0.024 | 37.84 | 8707 | 8.11 | 58 |  | 134.05 | 2.5 | 6.86 | -3.1 | 0.25 | 101
8/12/2025 11:30 | 6 | 19 | 2.75 | 7.709 | 2.798 | 7.14 | 53 | 1.98 | 69 | 0.293 | 0.024 | 37.84 | 8707 | 8.1 | 58 |  | 133.61 | 2.5 | 6.84 | -3.1 | 0.27 | 101
8/12/2025 11:45 | 6 | 19 | 2.75 | 7.68 | 2.856 | 7.14 | 53 | 1.98 | 69 | 0.293 | 0.024 | 37.84 | 8707 | 8.1 | 58 |  | 133.67 | 2.51 | 6.83 | -3.1 | 0.27 | 101
8/12/2025 12:00 | 8 | 19 | 2.75 | 7.705 | 2.959 | 7.13 | 53 | 1.98 | 69 | 0.201 | 0.024 | 37.84 | 8707 | 8.09 | 58 |  | 267.26 | 4.99 | 6.82 | -3.944 | 0.27 | 101
8/12/2025 12:15 | 9 | 19 | 2.75 | 7.677 | 2.87 | 7.12 | 53 | 1.98 | 69 | 0.201 | 0.024 | 37.84 | 8707 | 8.09 | 58 |  | 267.63 | 5.02 | 6.82 | -3.944 | 0.26 | 101
8/12/2025 12:30 | 9 | 19 | 2.75 | 7.727 | 2.681 | 7.12 | 53 | 1.98 | 69 | 0.201 | 0.024 | 37.84 | 8707 | 8.04 | 58 |  | 268.19 | 5 | 6.82 | -3.944 | 0.99 | 101
8/12/2025 12:45 | 9 | 19 | 2.75 | 7.739 | 2.574 | 7.12 | 53 | 1.98 | 69 | 0.201 | 0.024 | 37.84 | 8707 | 7.99 | 58 |  | 268.62 | 5 | 6.82 | -3.944 | 0.28 | 101
8/12/2025 13:00 | 8 | 19 | 2.75 | 7.753 | 2.542 | 7.12 | 53 | 1.98 | 69 | 0.201 | 0.024 | 37.84 | 8707 | 8 | 58 |  | 268.42 | 4.99 | 6.83 | -3.944 | 0.27 | 101
8/12/2025 13:15 | 10 | 19 | 2.75 | 7.733 | 2.709 | 7.12 | 53 | 1.98 | 69 | 0.201 | 0.024 | 37.84 | 8707 | 8.03 | 58 |  | 269.36 | 5.02 | 6.82 | -3.944 | 0.25 | 101
8/12/2025 13:30 | 11 | 19 | 2.75 | 7.748 | 2.454 | 7.11 | 53 | 1.98 | 69 | 0.201 | 0.024 | 37.84 | 8707 | 8.06 | 58 |  | 268.19 | 4.98 | 6.82 | -3.944 | 0.26 | 101
8/12/2025 13:45 | 11 | 19 | 2.75 | 7.703 | 2.545 | 7.11 | 53 | 1.98 | 69 | 0.201 | 0.024 | 37.84 | 8707 | 8.08 | 58 |  | 334.13 | 6.25 | 6.81 | -3.944 | 0.26 | 101
8/12/2025 14:00 | 12 | 19 | 2.75 | 7.761 | 4.555 | 7.11 | 53 | 1.98 | 69.4 | 0.201 | 0.024 | 37.84 | 8707 | 8.1 | 57 |  | 331.4 | 6.15 | 6.81 | -3.944 | 0.33 | 101
8/12/2025 14:15 | 7 | 19 | 2.75 | 7.76 | 3.687 | 7.11 | 53 | 1.98 | 69.4 | 0.201 | 0.024 | 37.84 | 8707 | 8.1 | 57 |  | 332.39 | 6.17 | 6.82 | -3.944 | 0.29 | 101
8/12/2025 14:30 | 9 | 19 | 2.75 | 7.782 | 3.451 | 7.11 | 53 | 1.98 | 69.4 | 0.201 | 0.024 | 37.84 | 8707 | 8.1 | 57 |  | 331.43 | 6.13 | 6.83 | -3.944 | 0.31 | 101
8/12/2025 14:45 | 10 | 19 | 2.75 | 7.166 | 3.181 | 7.11 | 53 | 1.98 | 69.4 | 0.201 | 0.024 | 37.84 | 8707 | 8.1 | 57 |  | 330.95 | 6.65 | 6.82 | -3.944 | 0.26 | 101
8/12/2025 15:00 | 14 | 19 | 2.75 | 7.119 | 2.902 | 7.11 | 53 | 1.98 | 69.4 | 0.201 | 0.024 | 37.84 | 8707 | 8.09 | 57 |  | 332.04 | 6.72 | 6.84 | -3.944 | 0.26 | 99
8/12/2025 15:15 | 11 | 19 | 2.75 | 7.377 | 2.709 | 7.1 | 53 | 1.98 | 69.4 | 0.201 | 0.024 | 37.84 | 8707 | 8.08 | 57 |  | 332.29 | 6.49 | 6.83 | -3.944 | 0.26 | 101
8/12/2025 15:30 | 12 | 19 | 2.75 | 7.382 | 2.629 | 7.1 | 53 | 1.98 | 69.4 | 0.201 | 0.023 | 37.84 | 8707 | 8.08 | 57 |  | 332.42 | 6.48 | 6.83 | -3.944 | 0.29 | 100
8/12/2025 15:45 | 13 | 19 | 2.75 | 7.346 | 2.503 | 7.11 | 53 | 1.98 | 69.4 | 0.201 | 0.023 | 37.84 | 8707 | 8.08 | 57 |  | 332.36 | 6.52 | 6.83 | -3.944 | 0.28 | 101
8/12/2025 16:00 | 10 | 19 | 2.75 | 7.362 | 2.543 | 7.13 | 53 | 1.98 | 69.4 | 0.194 | 0.023 | 37.84 | 8707 | 8.08 | 57 |  | 175.59 | 3.43 | 6.83 | -3.944 | 0.26 | 101
8/12/2025 16:15 | 12 | 19 | 2.75 | 7.339 | 2.636 | 7.13 | 53 | 1.98 | 69.4 | 0.194 | 0.023 | 37.84 | 8707 | 8.08 | 57 |  | 176.45 | 3.46 | 6.83 | -3.944 | 0.26 | 101
8/12/2025 16:30 | 12 | 19 | 2.75 | 7.333 | 2.761 | 7.11 | 53 | 1.98 | 69.4 | 0.194 | 0.023 | 37.84 | 8707 | 8.08 | 57 |  | 175.88 | 3.45 | 6.82 | -3.944 | 0.26 | 101
8/12/2025 16:45 | 12 | 19 | 2.75 | 7.303 | 2.762 | 7.12 | 53 | 1.98 | 69.4 | 0.194 | 0.023 | 37.84 | 8707 | 8.08 | 57 |  | 176.63 | 3.48 | 6.82 | -3.944 | 0.44 | 101
8/12/2025 17:00 | 12 | 19 | 2.75 | 7.323 | 2.514 | 7.13 | 53 | 1.98 | 69.4 | 0.194 | 0.023 | 37.84 | 8707 | 8.09 | 57 |  | 175.86 | 3.46 | 6.83 | -3.944 | 0.27 | 101
8/12/2025 17:15 | 12 | 19 | 2.75 | 7.823 | 2.546 | 7.13 | 53 | 1.98 | 69.4 | 0.194 | 0.023 | 37.84 | 8707 | 8.09 | 57 |  | 176.64 | 3.25 | 6.84 | -3.944 | 0.27 | 101
8/12/2025 17:30 | 12 | 19 | 2.75 | 7.815 | 2.406 | 7.14 | 53 | 1.98 | 69.4 | 0.194 | 0.023 | 37.84 | 8707 | 8.09 | 57 |  | 176.74 | 3.26 | 6.83 | -3.944 | 0.26 | 101
8/12/2025 17:45 | 12 | 19 | 2.75 | 7.83 | 2.405 | 7.14 | 53 | 1.98 | 69.4 | 0.194 | 0.023 | 37.84 | 8707 | 8.1 | 57 |  | 176.29 | 3.24 | 6.83 | -3.944 | 0.26 | 101
8/12/2025 18:00 | 8 | 19 | 2.75 | 7.765 | 2.324 | 7.15 | 53 | 1.98 | 69.8 | 0.194 | 0.023 | 37.84 | 8707 | 8.11 | 57 |  | 176.66 | 3.28 | 6.84 | -3.944 | 0.27 | 101
8/12/2025 18:15 | 13 | 19 | 2.75 | 7.249 | 2.088 | 7.16 | 53 | 1.98 | 69.8 | 0.194 | 0.023 | 37.84 | 8707 | 8.11 | 57 |  | 175.5 | 3.49 | 6.87 | -3.944 | 0.26 | 101
8/12/2025 18:30 | 12 | 19 | 2.75 | 7.565 | 2.125 | 7.16 | 53 | 1.98 | 69.8 | 0.194 | 0.023 | 37.84 | 8707 | 8.1 | 57 |  | 176.21 | 3.35 | 6.86 | -3.944 | 0.26 | 101
8/12/2025 18:45 | 11 | 19 | 2.75 | 7.595 | 2.1 | 7.16 | 53 | 1.98 | 69.8 | 0.194 | 0.024 | 37.84 | 8707 | 8.1 | 57 |  | 176.04 | 3.34 | 6.85 | -3.944 | 0.26 | 101
8/12/2025 19:00 | 10 | 19 | 2.75 | 7.589 | 2.155 | 7.17 | 53 | 1.98 | 69.8 | 0.194 | 0.024 | 37.84 | 8707 | 8.09 | 57 |  | 176.35 | 3.35 | 6.82 | -3.944 | 0.26 | 101
8/12/2025 19:15 | 12 | 19 | 2.75 | 7.618 | 2.174 | 7.17 | 53 | 1.98 | 69.8 | 0.194 | 0.024 | 37.84 | 8707 | 8.1 | 57 |  | 175.94 | 3.33 | 6.8 | -3.944 | 0.26 | 101
8/12/2025 19:30 | 13 | 19 | 2.75 | 7.583 | 2.143 | 7.16 | 53 | 1.98 | 69.8 | 0.194 | 0.024 | 37.84 | 8707 | 8.1 | 57 |  | 176.51 | 3.35 | 6.78 | -3.944 | 0.26 | 101
8/12/2025 19:45 | 13 | 19 | 2.75 | 7.59 | 2.154 | 7.16 | 53 | 1.98 | 69.8 | 0.194 | 0.023 | 37.84 | 8707 | 8.1 | 57 |  | 175.46 | 3.33 | 6.79 | -3.944 | 0.26 | 100
8/12/2025 20:00 | 8 | 19 | 2.75 | 7.601 | 2.207 | 7.14 | 53 | 1.98 | 69.8 | 0.17 | 0.024 | 37.84 | 8707 | 8.1 | 57 |  | 179.56 | 3.4 | 6.76 | -3.944 | 0.26 | 101
8/12/2025 20:15 | 9 | 19 | 2.75 | 7.572 | 2.757 | 7.14 | 53 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.1 | 57 |  | 179.55 | 3.41 | 6.78 | -3.944 | 0.26 | 101
8/12/2025 20:30 | 9 | 19 | 2.75 | 7.6 | 2.618 | 7.13 | 53 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.1 | 57 |  | 179.49 | 3.4 | 6.81 | -3.944 | 0.26 | 101
8/12/2025 20:45 | 9 | 19 | 2.75 | 7.579 | 2.483 | 7.12 | 53 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.11 | 57 |  | 179.32 | 3.41 | 6.83 | -3.944 | 0.25 | 101
8/12/2025 21:00 | 11 | 19 | 2.75 | 6.914 | 2.544 | 7.12 | 53 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.1 | 57 |  | 168.55 | 3.51 | 6.87 | -3.944 | 0.24 | 101
8/12/2025 21:15 | 11 | 19 | 2.75 | 7.569 | 2.274 | 7.13 | 53 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.1 | 57 |  | 179.48 | 3.41 | 6.87 | -3.944 | 0.25 | 101
8/12/2025 21:30 | 8 | 19 | 2.75 | 7.532 | 2.158 | 7.14 | 53 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.1 | 57 |  | 179.42 | 3.43 | 6.86 | -3.944 | 0.24 | 101
8/12/2025 21:45 | 11 | 19 | 2.75 | 7.569 | 2.022 | 7.15 | 53 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.1 | 57 |  | 179.8 | 3.42 | 6.87 | -3.944 | 0.26 | 101
8/12/2025 22:00 | 10 | 19 | 2.75 | 7.538 | 1.984 | 7.16 | 55 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.11 | 57 |  | 179.08 | 3.42 | 6.86 | -3.944 | 0.25 | 101
8/12/2025 22:15 | 10 | 19 | 2.75 | 7.557 | 2.013 | 7.17 | 55 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.11 | 57 |  | 179.02 | 3.41 | 6.86 | -3.944 | 0.24 | 101
8/12/2025 22:30 | 10 | 19 | 2.75 | 7.075 | 1.95 | 7.18 | 55 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.11 | 57 |  | 171.42 | 3.49 | 6.86 | -3.944 | 0.24 | 101
8/12/2025 22:45 | 9 | 19 | 2.75 | 7.127 | 2.033 | 7.17 | 55 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.12 | 57 |  | 172.86 | 3.49 | 6.86 | -3.944 | 0.24 | 101
8/12/2025 23:00 | 9 | 19 | 2.75 | 7.288 | 2.119 | 7.16 | 55 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.13 | 57 |  | 176.56 | 3.49 | 6.84 | -3.944 | 0.23 | 101
8/12/2025 23:15 | 10 | 19 | 2.75 | 7.309 | 2.305 | 7.17 | 55 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.14 | 57 |  | 101.75 | 2 | 6.83 | -3.944 | 0.24 | 101
8/12/2025 23:30 | 10 | 19 | 2.75 | 7.572 | 2.399 | 7.17 | 55 | 1.98 | 69.8 | 0.17 | 0.023 | 37.84 | 8707 | 8.15 | 57 |  | 105.18 | 2 | 6.81 | -3.944 | 0.25 | 101
8/12/2025 23:45 | 9 | 19 | 2.75 | 7.841 | 2.24 | 7.18 | 55 | 1.98 | 69.8 | 0.17 | 0.024 | 39.07 | 8845 | 8.16 | 57 |  | 109.03 | 2 | 6.81 | -3.944 | 0.24 | 101
8/13/2025 00:00 | 10 | 19 | 2.75 | 7.82 | 2.304 | 7.19 | 55 | 1.98 | 69.8 | 0.218 | 0.024 | 39.07 | 8845 | 8.17 | 57 |  | 108.98 | 2.01 | 6.82 | -3.944 | 0.25 | 101
8/13/2025 00:15 | 10 | 19 | 2.75 | 7.844 | 2.222 | 7.19 | 55 | 1.98 | 69.8 | 0.218 | 0.025 | 39.07 | 8845 | 8.17 | 57 |  | 108.95 | 2 | 6.82 | -3.944 | 0.25 | 101
8/13/2025 00:30 | 11 | 19 | 2.75 | 7.831 | 2.229 | 7.18 | 55 | 1.98 | 69.8 | 0.218 | 0.024 | 39.07 | 8845 | 8.17 | 57 |  | 109.02 | 2 | 6.82 | -3.944 | 0.24 | 101
8/13/2025 00:45 | 10 | 19 | 2.75 | 7.826 | 2.471 | 7.17 | 55 | 1.98 | 69.8 | 0.218 | 0.024 | 39.07 | 8845 | 8.14 | 57 |  | 108.87 | 2 | 6.81 | -3.944 | 0.25 | 101
8/13/2025 01:00 | 10 | 19 | 2.75 | 7.52 | 2.533 | 7.16 | 55 | 1.98 | 69.8 | 0.218 | 0.024 | 39.07 | 8845 | 8.13 | 57 |  | 105.09 | 2.01 | 6.81 | -3.944 | 0.24 | 101
8/13/2025 01:15 | 8 | 19 | 2.75 | 7.295 | 2.488 | 7.16 | 55 | 1.98 | 69.8 | 0.218 | 0.024 | 39.07 | 8845 | 8.15 | 57 |  | 100.98 | 1.99 | 6.83 | -3.944 | 0.24 | 101
8/13/2025 01:30 | 8 | 19 | 2.75 | 7.76 | 2.444 | 7.18 | 55 | 1.98 | 69.8 | 0.218 | 0.024 | 39.07 | 8845 | 8.18 | 57 |  | 108.03 | 2 | 6.83 | -3.944 | 0.25 | 101
8/13/2025 01:45 | 5 | 19 | 2.75 | 7.797 | 2.453 | 7.17 | 55 | 1.98 | 69.8 | 0.218 | 0.024 | 39.07 | 8845 | 8.21 | 57 |  | 108 | 1.99 | 6.82 | -3.944 | 0.24 | 101
8/13/2025 02:00 | 9 | 19 | 2.75 | 7.767 | 2.4 | 7.16 | 55 | 1.98 | 69.6 | 0.218 | 0.024 | 39.07 | 8845 | 8.21 | 57 |  | 105.49 | 1.96 | 6.82 | -3.944 | 0.25 | 101
8/13/2025 02:15 | 7 | 19 | 2.75 | 7.786 | 2.341 | 7.16 | 55 | 1.98 | 69.6 | 0.218 | 0.024 | 39.07 | 8845 | 8.21 | 57 |  | 108.17 | 2 | 6.82 | -3.944 | 0.27 | 101
8/13/2025 02:30 | 8 | 19 | 2.75 | 7.754 | 9.036 | 7.15 | 55 | 1.98 | 69.6 | 0.218 | 0.024 | 39.07 | 8845 | 8.2 | 57 |  | 108.05 | 2.01 | 6.81 | -3.944 | 0.24 | 101
8/13/2025 02:45 | 7 | 19 | 2.75 | 7.395 | 4.178 | 7.13 | 55 | 1.98 | 69.6 | 0.218 | 0.023 | 39.07 | 8845 | 8.19 | 57 |  | 154.49 | 3.01 | 6.8 | -3.944 | 0.24 | 101
8/13/2025 03:00 | 7 | 19 | 2.75 | 7.218 | 3.159 | 7.12 | 55 | 1.98 | 69.6 | 0.218 | 0.023 | 39.07 | 8845 | 8.19 | 57 |  | 149.49 | 2.98 | 6.81 | -3.944 | 0.59 | 101
8/13/2025 03:15 | 6 | 19 | 2.75 | 7.745 | 2.797 | 7.12 | 55 | 1.98 | 69.6 | 0.218 | 0.023 | 39.07 | 8845 | 8.19 | 57 |  | 161.56 | 3 | 6.8 | -3.944 | 0.35 | 101
8/13/2025 03:30 | 5 | 19 | 2.75 | 7.728 | 2.693 | 7.12 | 55 | 1.98 | 69.6 | 0.218 | 0.023 | 39.07 | 8845 | 8.19 | 57 |  | 160.97 | 3 | 6.78 | -3.944 | 0.26 | 101
8/13/2025 03:45 | 8 | 19 | 2.75 | 7.738 | 2.69 | 7.11 | 55 | 1.98 | 69.6 | 0.218 | 0.023 | 39.07 | 8845 | 8.19 | 57 |  | 161.42 | 3 | 6.79 | -3.944 | 0.26 | 101
8/13/2025 04:00 | 9 | 19 | 2.75 | 7.748 | 2.658 | 7.12 | 55 | 1.98 | 69.6 | 0.262 | 0.023 | 39.07 | 8845 | 8.19 | 57 |  | 160.34 | 2.98 | 6.81 | -3.944 | 0.25 | 101
8/13/2025 04:15 | 6 | 19 | 2.75 | 7.168 | 2.563 | 7.12 | 55 | 1.98 | 69.6 | 0.262 | 0.023 | 39.07 | 8845 | 8.19 | 57 |  | 149.34 | 3 | 6.83 | -3.944 | 0.3 | 101
8/13/2025 04:30 | 9 | 19 | 2.75 | 7.499 | 2.729 | 7.11 | 55 | 1.98 | 69.6 | 0.262 | 0.023 | 39.07 | 8845 | 8.18 | 57 |  | 155.85 | 2.99 | 6.83 | -3.944 | 0.24 | 101
8/13/2025 04:45 | 5 | 19 | 2.75 | 7.471 | 2.631 | 7.11 | 55 | 1.98 | 69.6 | 0.262 | 0.023 | 39.07 | 8845 | 8.18 | 57 |  | 155.89 | 3 | 6.8 | -3.944 | 0.24 | 101
8/13/2025 05:00 | 7 | 19 | 2.75 | 7.491 | 2.616 | 7.11 | 55 | 1.98 | 69.6 | 0.262 | 0.023 | 39.07 | 8845 | 8.18 | 57 |  | 155.94 | 3 | 6.81 | -3.944 | 0.24 | 101
8/13/2025 05:15 | 7 | 19 | 2.75 | 7.482 | 2.666 | 7.11 | 55 | 1.98 | 69.6 | 0.262 | 0.023 | 39.07 | 8845 | 8.18 | 57 |  | 103.93 | 2 | 6.81 | -3.944 | 0.25 | 101
8/13/2025 05:30 | 8 | 19 | 2.75 | 7.473 | 2.735 | 7.12 | 55 | 1.98 | 69.6 | 0.262 | 0.023 | 39.07 | 8845 | 8.18 | 57 |  | 103.81 | 2 | 6.81 | -3.944 | 0.24 | 101
8/13/2025 05:45 | 6 | 19 | 2.75 | 7.502 | 2.783 | 7.12 | 55 | 1.98 | 69.6 | 0.262 | 0.023 | 39.07 | 8845 | 8.18 | 57 |  | 103.77 | 1.99 | 6.81 | -3.944 | 0.24 | 101
8/13/2025 06:00 | 1 | 19 | 2.75 | 7.484 | 2.808 | 7.13 | 55 | 1.98 | 69.4 | 0.262 | 0.023 | 39.07 | 8845 | 8.18 | 57 |  | 104.2 | 2 | 6.81 | -3.944 | 0.23 | 101
8/13/2025 06:15 | 7 | 19 | 2.75 | 8.164 | 2.793 | 7.13 | 55 | 1.98 | 69.4 | 0.262 | 0.022 | 39.07 | 8845 | 8.18 | 57 |  | 113.14 | 2 | 6.8 | -3.944 | 0.26 | 101
8/13/2025 06:30 | 8 | 19 | 2.75 | 8.151 | 2.991 | 7.13 | 55 | 1.98 | 69.4 | 0.262 | 0.023 | 39.07 | 8845 | 8.18 | 57 |  | 84.89 | 1.5 | 6.79 | -3.944 | 0.25 | 101
8/13/2025 06:45 | 7 | 19 | 2.75 | 8.342 | 2.996 | 7.13 | 55 | 1.98 | 69.4 | 0.262 | 0.023 | 39.07 | 8845 | 8.18 | 57 |  | 86.66 | 1.5 | 6.79 | -3.944 | 0.26 | 101
8/13/2025 07:00 | 8 | 19 | 2.75 | 8.355 | 2.978 | 7.12 | 55 | 1.98 | 69.4 | 0.262 | 0.023 | 39.07 | 8845 | 8.18 | 57 |  | 87.06 | 1.5 | 6.8 | -3.944 | 0.24 | 101
8/13/2025 07:15 | 7 | 19 | 2.75 | 8.353 | 2.927 | 7.13 | 55 | 1.98 | 69.4 | 0.262 | 0.023 | 39.07 | 8845 | 8.18 | 57 |  | 86.86 | 1.5 | 6.81 | -3.944 | 0.25 | 101
8/13/2025 07:30 | 8 | 19 | 2.75 | 8.397 | 2.929 | 7.14 | 55 | 1.98 | 69.4 | 0.262 | 0.023 | 39.07 | 8845 | 8.18 | 57 |  | 87.2 | 1.5 | 6.82 | -3.944 | 0.25 | 101
8/13/2025 07:45 | 8 | 19 | 2.75 | 7.888 | 3.001 | 7.15 | 55 | 1.98 | 69.4 | 0.262 | 0.023 | 39.07 | 8845 | 8.19 | 57 |  | 82.1 | 1.5 | 6.83 | -3.944 | 0.24 | 101
8/13/2025 08:00 | 10 | 19 | 2.75 | 7.641 | 3.11 | 7.15 | 55 | 1.98 | 69.4 | 0.283 | 0.023 | 39.07 | 8845 | 8.21 | 57 |  | 79.14 | 1.49 | 6.85 | -3.944 | 0.24 | 101
8/13/2025 08:15 | 5 | 19 | 2.75 | 7.877 | 3.134 | 7.15 | 55 | 1.98 | 69.4 | 0.283 | 0.023 | 39.07 | 8845 | 8.22 | 57 |  | 81.89 | 1.5 | 6.84 | -3.944 | 0.24 | 101
8/13/2025 08:30 | 6 | 19 | 2.75 | 7.895 | 3.203 | 7.15 | 55 | 1.98 | 69.4 | 0.283 | 0.023 | 39.07 | 8845 | 8.22 | 57 |  | 82.2 | 1.5 | 6.84 | -3.944 | 0.24 | 101
8/13/2025 08:45 | 5 | 19 | 2.75 | 7.879 | 3.312 | 7.15 | 55 | 1.98 | 69.4 | 0.283 | 0.022 | 39.07 | 8845 | 8.21 | 57 |  | 82.02 | 1.5 | 6.83 | -3.944 | 0.25 | 101
8/13/2025 09:00 | 5 | 19 | 2.75 | 7.9 | 3.173 | 7.16 | 55 | 1.98 | 69.4 | 0.283 | 0.022 | 39.07 | 8845 | 8.2 | 57 |  | 82.06 | 1.5 | 6.83 | -3.944 | 0.25 | 101
8/13/2025 09:15 | 4 | 19 | 2.75 | 7.86 | 3.229 | 7.16 | 55 | 1.98 | 69.4 | 0.283 | 0.022 | 39.07 | 8845 | 8.18 | 57 |  | 81.7 | 1.5 | 6.84 | -3.944 | 0.25 | 101
8/13/2025 09:30 | 6 | 19 | 2.75 | 7.874 | 3.062 | 7.17 | 55 | 1.98 | 69.4 | 0.283 | 0.022 | 39.07 | 8845 | 8.17 | 57 |  | 82.25 | 1.5 | 6.84 | -3.944 | 0.25 | 101
8/13/2025 09:45 | 4 | 19 | 2.75 | 7.857 | 3.027 | 7.17 | 55 | 1.98 | 69.4 | 0.283 | 0.022 | 39.07 | 8845 | 8.17 | 57 |  | 82.13 | 1.51 | 6.84 | -3.944 | 0.25 | 101
8/13/2025 10:00 | 6 | 19 | 2.75 | 7.849 | 2.927 | 7.17 | 54 | 1.98 | 69.6 | 0.283 | 0.022 | 39.07 | 8845 | 8.16 | 57 |  | 82.69 | 1.52 | 6.84 | -3.944 | 0.25 | 101
8/13/2025 10:15 | -1 | 19 | 2.75 | 7.891 | 3.002 | 7.17 | 54 | 1.98 | 69.6 | 0.283 | 0.022 | 39.07 | 8845 | 8.16 | 57 |  | 81.8 | 1.49 | 6.84 | -3.944 | 0.25 | 101
8/13/2025 10:30 | 3 | 19 | 2.75 | 7.892 | 2.877 | 7.17 | 54 | 1.98 | 69.6 | 0.283 | 0.022 | 39.07 | 8845 | 8.16 | 57 |  | 81.97 | 1.5 | 6.84 | -3.944 | 0.26 | 101
8/13/2025 10:45 | 8 | 19 | 2.75 | 7.877 | 2.938 | 7.17 | 54 | 1.98 | 69.6 | 0.283 | 0.022 | 39.07 | 8845 | 8.16 | 57 |  | 81.75 | 1.49 | 6.83 | -3.944 | 0.25 | 101
8/13/2025 11:00 | 7 | 19 | 2.75 | 7.865 | 3.027 | 7.17 | 54 | 1.98 | 69.6 | 0.283 | 0.022 | 39.07 | 8845 | 8.16 | 57 |  | 82.17 | 1.5 | 6.83 | -3.944 | 0.2 | 101
8/13/2025 11:15 | 2 | 19 | 2.75 | 7.892 | 3.015 | 7.17 | 54 | 1.98 | 69.6 | 0.283 | 0.022 | 39.07 | 8845 | 8.16 | 57 |  | 81.74 | 1.49 | 6.83 | -3.944 | 0.21 | 101
8/13/2025 11:30 | 6 | 19 | 2.75 | 7.898 | 2.982 | 7.17 | 54 | 1.98 | 69.6 | 0.283 | 0.022 | 39.07 | 8845 | 8.17 | 57 |  | 82.66 | 1.51 | 6.83 | -3.944 | 0.21 | 101
8/13/2025 11:45 | 6 | 19 | 2.75 | 7.878 | 2.981 | 7.17 | 54 | 1.98 | 69.6 | 0.283 | 0.022 | 39.07 | 8845 | 8.17 | 57 |  | 81.93 | 1.5 | 6.8 | -3.944 | 0.22 | 101
8/13/2025 12:00 | 2 | 19 | 2.75 | 7.921 | 2.488 | 7.11 | 54 | 1.98 | 69.6 | 0.151 | 0.022 | 39.07 | 8845 | 8.17 | 57 |  | 81.91 | 1.49 | 6.76 | -3.944 | 0.2 | 101
8/13/2025 12:15 | 2 | 19 | 2.75 | 7.866 | 2.518 | 7.15 | 54 | 1.98 | 69.6 | 0.151 | 0.022 | 39.07 | 8845 | 8.17 | 57 |  | 81.96 | 1.5 | 6.81 | -3.944 | 0.22 | 101
8/13/2025 12:30 | 6 | 19 | 2.75 | 7.899 | 2.333 | 7.18 | 54 | 1.98 | 69.6 | 0.151 | 0.022 | 39.07 | 8845 | 8.17 | 57 |  | 82.2 | 1.5 | 6.88 | -3.944 | 0.23 | 101
8/13/2025 12:45 | 3 | 19 | 2.75 | 8.279 | 2.359 | 7.19 | 54 | 1.98 | 69.6 | 0.151 | 0.022 | 39.07 | 8845 | 8.17 | 57 |  | 86.84 | 1.51 | 6.87 | -3.944 | 0.24 | 101
8/13/2025 13:00 | 7 | 19 | 2.75 | 7.021 | 2.38 | 7.19 | 54 | 1.98 | 69.6 | 0.151 | 0.022 | 40.97 | 9443 | 8.17 | 57 |  | 72.83 | 1.49 | 6.87 | -3.944 | 0.24 | 101
8/13/2025 13:15 | 6 | 19 | 2.75 | 7.015 | 2.468 | 7.18 | 54 | 1.98 | 69.6 | 0.151 | 0.022 | 40.97 | 9443 | 8.17 | 57 |  | 72.82 | 1.49 | 6.85 | -3.944 | 0.24 | 101
8/13/2025 13:30 | 6 | 19 | 2.75 | 7.299 | 2.796 | 7.17 | 54 | 1.98 | 69.6 | 0.151 | 0.023 | 40.97 | 9443 | 8.16 | 57 |  | 75.42 | 1.49 | 6.86 | -3.944 | 0.22 | 101
8/13/2025 13:45 | 8 | 19 | 2.75 | 7.268 | 2.478 | 7.17 | 54 | 1.98 | 69.6 | 0.151 | 0.022 | 40.97 | 9443 | 8.15 | 57 |  | 75.76 | 1.5 | 6.86 | -3.944 | 0.24 | 101
8/13/2025 14:00 | 5 | 19 | 2.75 | 7.503 | 2.462 | 7.17 | 54 | 1.98 | 69.9 | 0.151 | 0.022 | 40.97 | 9443 | 8.14 | 56 |  | 78.28 | 1.5 | 6.85 | -3.944 | 0.24 | 101
8/13/2025 14:15 | 6 | 19 | 2.75 | 7.503 | 2.424 | 7.17 | 54 | 1.98 | 69.9 | 0.151 | 0.022 | 40.97 | 9443 | 8.1 | 56 |  | 78.22 | 1.5 | 6.85 | -3.944 | 0.25 | 101
8/13/2025 14:30 | 7 | 19 | 2.75 | 7.531 | 2.581 | 7.17 | 54 | 1.98 | 69.9 | 0.151 | 0.022 | 40.97 | 9443 | 8.07 | 56 |  | 78.58 | 1.5 | 6.84 | -3.944 | 0.24 | 101
8/13/2025 14:45 | 8 | 19 | 2.75 | 7.518 | 2.518 | 7.17 | 54 | 1.98 | 69.9 | 0.151 | 0.022 | 40.97 | 9443 | 8.08 | 56 |  | 78.23 | 1.5 | 6.85 | -3.944 | 0.24 | 101
8/13/2025 15:00 | 9 | 19 | 2.75 | 7.498 | 2.607 | 7.18 | 54 | 1.98 | 69.9 | 0.151 | 0.022 | 40.97 | 9443 | 8.11 | 56 |  | 78.46 | 1.51 | 6.85 | -3.944 | 0.24 | 101
8/13/2025 15:15 | 9 | 19 | 2.75 | 7.785 | 2.676 | 7.18 | 54 | 1.98 | 69.9 | 0.151 | 0.022 | 40.97 | 9443 | 8.13 | 56 |  | 80.89 | 1.5 | 6.85 | -3.944 | 0.25 | 101
8/13/2025 15:30 | 8 | 19 | 2.75 | 7.731 | 2.639 | 7.18 | 54 | 1.98 | 69.9 | 0.151 | 0.023 | 41.26 | 9473 | 8.14 | 56 |  | 80.78 | 1.5 | 6.85 | -3.944 | 0.25 | 101
8/13/2025 15:45 | 9 | 19 | 2.75 | 7.206 | 2.596 | 7.18 | 54 | 1.98 | 69.9 | 0.151 | 0.024 | 41.26 | 9473 | 8.15 | 56 |  | 72.65 | 1.45 | 6.85 | -3.944 | 0.25 | 101
8/13/2025 16:00 | 7 | 19 | 2.75 | 7.595 | 2.508 | 7.18 | 54 | 1.98 | 69.9 | 0.153 | 0.024 | 41.26 | 9473 | 8.15 | 56 |  | 78.74 | 1.49 | 6.86 | -3.944 | 0.25 | 101
8/13/2025 16:15 | 5 | 19 | 2.75 | 7.609 | 2.582 | 7.17 | 54 | 1.98 | 69.9 | 0.153 | 0.024 | 41.26 | 9473 | 8.14 | 56 |  | 79.34 | 1.5 | 6.84 | -3.944 | 0.24 | 101
8/13/2025 16:30 | 11 | 19 | 2.75 | 7.625 | 2.555 | 7.18 | 54 | 1.98 | 69.9 | 0.153 | 0.024 | 41.26 | 9473 | 8.12 | 56 |  | 78.94 | 1.49 | 6.85 | -3.944 | 0.25 | 101
8/13/2025 16:45 | 11 | 19 | 2.75 | 7.601 | 2.568 | 7.18 | 54 | 1.98 | 69.9 | 0.153 | 0.024 | 41.26 | 9473 | 8.11 | 56 |  | 78.9 | 1.49 | 6.85 | -3.944 | 0.25 | 101
8/13/2025 17:00 | 3 | 19 | 2.75 | 7.587 | 2.868 | 7.16 | 54 | 1.98 | 69.9 | 0.153 | 0.023 | 41.26 | 9473 | 8.12 | 56 |  | 79.21 | 1.5 | 6.83 | -3.944 | 0.24 | 101
8/13/2025 17:15 | 7 | 19 | 2.75 | 7.586 | 2.703 | 7.17 | 54 | 1.98 | 69.9 | 0.153 | 0.023 | 41.26 | 9473 | 8.15 | 56 |  | 79.03 | 1.5 | 6.83 | -3.944 | 0.24 | 101
8/13/2025 17:30 | 9 | 19 | 2.75 | 7.598 | 2.911 | 7.16 | 54 | 1.98 | 69.9 | 0.153 | 0.024 | 41.26 | 9473 | 8.17 | 56 |  | 79.3 | 1.5 | 6.83 | -3.944 | 0.25 | 101
8/13/2025 17:45 | 10 | 19 | 2.75 | 7.649 | 2.805 | 7.19 | 54 | 1.98 | 69.9 | 0.153 | 0.024 | 41.26 | 9473 | 8.18 | 56 |  | 78.81 | 1.48 | 6.86 | -3.944 | 0.24 | 101
8/13/2025 18:00 | 11 | 19 | 2.75 | 7.553 | 3.089 | 7.19 | 54 | 1.98 | 70.1 | 0.153 | 0.024 | 41.26 | 9473 | 8.18 | 56 |  | 78.87 | 1.5 | 6.86 | -3.944 | 0.25 | 101
8/13/2025 18:15 | 9 | 19 | 2.75 | 7.46 | 2.746 | 7.19 | 54 | 1.98 | 70.1 | 0.153 | 0.024 | 41.26 | 9473 | 8.18 | 56 |  | 77.73 | 1.5 | 6.86 | -3.944 | 0.25 | 101
8/13/2025 18:30 | 13 | 19 | 2.75 | 7.146 | 2.879 | 7.18 | 54 | 1.98 | 70.1 | 0.153 | 0.024 | 41.26 | 9473 | 8.18 | 56 |  | 75.24 | 1.52 | 6.85 | -3.944 | 0.25 | 101
8/13/2025 18:45 | 9 | 19 | 2.75 | 7.455 | 2.736 | 7.18 | 54 | 1.98 | 70.1 | 0.153 | 0.024 | 41.26 | 9473 | 8.18 | 56 |  | 124.38 | 2.4 | 6.85 | -3.944 | 0.25 | 101
8/13/2025 19:00 | 11 | 19 | 2.75 | 7.507 | 2.6 | 7.15 | 54 | 1.98 | 70.1 | 0.153 | 0.024 | 41.26 | 9473 | 8.18 | 56 |  | 129.36 | 2.48 | 6.85 | -3.944 | 0.25 | 101
8/13/2025 19:15 | 6 | 19 | 2.75 | 7.472 | 20.307 | 7.17 | 54 | 1.98 | 70.1 | 0.153 | 0.024 | 41.26 | 9473 | 8.17 | 56 |  | 130.44 | 2.51 | 6.85 | -3.944 | 0.27 | 101
8/13/2025 19:30 | 12 | 19 | 2.75 | 7.498 | 5.748 | 7.18 | 54 | 1.98 | 70.1 | 0.153 | 0.024 | 41.26 | 9473 | 8.16 | 56 |  | 130.36 | 2.5 | 6.85 | -3.944 | 0.26 | 101
8/13/2025 19:45 | 10 | 19 | 2.75 | 7.484 | 4.087 | 7.17 | 54 | 1.98 | 70.1 | 0.153 | 0.024 | 41.26 | 9473 | 8.16 | 56 |  | 129.74 | 2.5 | 6.84 | -3.944 | 0.24 | 101
8/13/2025 20:00 | 7 | 19 | 2.75 | 7.725 | 3.551 | 7.16 | 54 | 1.98 | 70.1 | 0.168 | 0.024 | 41.26 | 9473 | 8.16 | 56 |  | 134.75 | 2.51 | 6.83 | -3.944 | 0.25 | 101
8/13/2025 20:15 | 12 | 19 | 2.75 | 7.73 | 2.973 | 7.16 | 54 | 1.98 | 70.1 | 0.168 | 0.024 | 41.26 | 9473 | 8.16 | 56 |  | 134.45 | 2.5 | 6.83 | -3.944 | 0.27 | 101
8/13/2025 20:30 | 13 | 19 | 2.75 | 7.699 | 2.321 | 7.16 | 54 | 1.98 | 70.1 | 0.168 | 0.024 | 41.26 | 9473 | 8.16 | 56 |  | 133.91 | 2.5 | 6.86 | -3.944 | 0.25 | 99
8/13/2025 20:45 | 11 | 19 | 2.75 | 7.088 | 2.59 | 7.14 | 54 | 1.98 | 70.1 | 0.168 | 0.024 | 41.26 | 9473 | 8.16 | 56 |  | 123.18 | 2.5 | 6.85 | -3.944 | 0.24 | 101
8/13/2025 21:00 | 13 | 19 | 2.75 | 7.105 | 2.424 | 7.13 | 54 | 1.98 | 70.1 | 0.168 | 0.029 | 41.47 | 9491 | 8.16 | 56 |  | 172.25 | 3.49 | 6.84 | -3.944 | 0.24 | 101
8/13/2025 21:15 | 9 | 19 | 2.75 | 7.341 | 2.387 | 7.14 | 54 | 1.98 | 70.1 | 0.168 | 0.028 | 41.47 | 9491 | 8.16 | 56 |  | 176.29 | 3.46 | 6.86 | -3.944 | 0.24 | 101
8/13/2025 21:30 | 6 | 19 | 2.75 | 7.327 | 2.538 | 7.13 | 54 | 1.98 | 70.1 | 0.168 | 0.026 | 41.47 | 9491 | 8.16 | 56 |  | 175.89 | 3.46 | 6.85 | -3.944 | 0.23 | 101
8/13/2025 21:45 | 9 | 19 | 2.75 | 7.292 | 2.47 | 7.13 | 54 | 1.98 | 70.1 | 0.168 | 0.025 | 41.47 | 9491 | 8.15 | 56 |  | 176.26 | 3.48 | 6.84 | -3.944 | 0.23 | 101
8/13/2025 22:00 | 9 | 19 | 2.75 | 7.326 | 2.671 | 7.12 | 55 | 1.98 | 69.9 | 0.168 | 0.025 | 41.47 | 9491 | 8.12 | 56 |  | 176.51 | 3.47 | 6.83 | -3.944 | 0.24 | 101
8/13/2025 22:15 | 9 | 19 | 2.75 | 7.31 | 2.737 | 7.12 | 55 | 1.98 | 69.9 | 0.168 | 0.025 | 41.47 | 9491 | 8.06 | 56 |  | 178.04 | 3.51 | 6.83 | -3.944 | 0.23 | 101
8/13/2025 22:30 | 10 | 19 | 2.75 | 7.584 | 4.45 | 7.12 | 55 | 1.98 | 69.9 | 0.168 | 0.025 | 41.47 | 9491 | 8.04 | 56 |  | 180.41 | 3.43 | 6.82 | -3.944 | 0.25 | 101
8/13/2025 22:45 | 11 | 19 | 2.75 | 7.567 | 3.115 | 7.13 | 55 | 1.98 | 69.9 | 0.168 | 0.025 | 41.47 | 9491 | 8.06 | 56 |  | 179.52 | 3.42 | 6.82 | -3.944 | 0.22 | 101
8/13/2025 23:00 | 10 | 19 | 2.75 | 7.85 | 2.72 | 7.12 | 55 | 1.98 | 69.9 | 0.168 | 0.025 | 41.47 | 9491 | 8.09 | 56 |  | 179.65 | 3.3 | 6.81 | -3.944 | 0.22 | 101
8/13/2025 23:15 | 9 | 19 | 2.75 | 7.812 | 2.64 | 7.12 | 55 | 1.98 | 69.9 | 0.168 | 0.025 | 41.47 | 9491 | 8.13 | 56 |  | 179.55 | 3.31 | 6.81 | -3.944 | 0.32 | 101
8/13/2025 23:30 | 10 | 19 | 2.75 | 7.796 | 2.841 | 7.11 | 55 | 1.98 | 69.9 | 0.168 | 0.025 | 41.47 | 9491 | 8.15 | 56 |  | 179.76 | 3.32 | 6.79 | -3.944 | 0.23 | 101
8/13/2025 23:45 | 9 | 19 | 2.75 | 7.362 | 2.866 | 7.11 | 55 | 1.98 | 69.9 | 0.168 | 0.025 | 41.47 | 9491 | 8.16 | 56 |  | 179.24 | 3.51 | 6.82 | -3.944 | 0.23 | 101
8/14/2025 00:00 | 10 | 19 | 2.75 | 7.381 | 2.68 | 7.12 | 55 | 1.98 | 69.9 | 0.268 | 0.025 | 41.47 | 9491 | 8.16 | 56 |  | 179.64 | 3.5 | 6.84 | -3.944 | 0.16 | 101
8/14/2025 00:15 | 11 | 19 | 2.75 | 7.98 | 2.656 | 7.12 | 55 | 1.98 | 69.9 | 0.268 | 0.025 | 41.47 | 9491 | 8.16 | 56 |  | 179.81 | 3.24 | 6.84 | -3.944 | 0.27 | 101
8/14/2025 00:30 | 9 | 19 | 2.75 | 7.954 | 2.752 | 7.11 | 55 | 1.98 | 69.9 | 0.268 | 0.025 | 42.54 | 9594 | 8.17 | 56 |  | 178.93 | 3.24 | 6.81 | -3.944 | 0.24 | 101
8/14/2025 00:45 | 8 | 19 | 2.75 | 7.863 | 2.997 | 7.11 | 55 | 1.98 | 69.9 | 0.268 | 0.025 | 42.54 | 9594 | 8.17 | 56 |  | 178.89 | 3.28 | 6.81 | -3.944 | 0.24 | 101
8/14/2025 01:00 | 10 | 19 | 2.75 | 7.417 | 2.841 | 7.11 | 55 | 1.98 | 69.9 | 0.268 | 0.026 | 42.54 | 9594 | 8.17 | 56 |  | 179.74 | 3.49 | 6.83 | -3.944 | 0.24 | 101
8/14/2025 01:15 | 7 | 19 | 2.75 | 7.48 | 2.801 | 7.11 | 55 | 1.98 | 69.9 | 0.268 | 0.026 | 42.54 | 9594 | 8.17 | 56 |  | 179.51 | 3.46 | 6.86 | -3.944 | 0.24 | 101
8/14/2025 01:30 | 10 | 19 | 2.75 | 7.903 | 2.706 | 7.12 | 55 | 1.98 | 69.9 | 0.268 | 0.026 | 42.54 | 9594 | 8.16 | 56 |  | 179.24 | 3.27 | 6.83 | -3.944 | 0.16 | 101
8/14/2025 01:45 | 13 | 19 | 2.75 | 7.896 | 2.587 | 7.11 | 55 | 1.98 | 69.9 | 0.268 | 0.026 | 42.54 | 9594 | 8.14 | 56 |  | 179.06 | 3.27 | 6.82 | -3.944 | 0.24 | 101
8/14/2025 02:00 | 5 | 19 | 2.75 | 7.899 | 2.578 | 7.11 | 55 | 1.98 | 69.9 | 0.268 | 0.026 | 42.54 | 9594 | 8.15 | 57 |  | 179.31 | 3.27 | 6.82 | -3.944 | 0.24 | 101
8/14/2025 02:15 | 9 | 19 | 2.75 | 7.934 | 2.907 | 7.1 | 55 | 1.98 | 69.9 | 0.268 | 0.026 | 42.54 | 9594 | 8.18 | 57 |  | 179 | 3.25 | 6.8 | -3.944 | 0.22 | 101
8/14/2025 02:30 | 9 | 19 | 2.75 | 8.248 | 3.068 | 7.09 | 55 | 1.98 | 69.9 | 0.268 | 0.026 | 42.54 | 9594 | 8.21 | 57 |  | 178.84 | 3.12 | 6.79 | -3.944 | 0.22 | 101
8/14/2025 02:45 | 11 | 19 | 2.75 | 8.235 | 3.099 | 7.09 | 55 | 1.98 | 69.9 | 0.268 | 0.026 | 42.54 | 9594 | 8.22 | 57 |  | 179.06 | 3.13 | 6.79 | -3.944 | 0.22 | 101
8/14/2025 03:00 | 8 | 19 | 2.75 | 8.213 | 3.125 | 7.09 | 55 | 1.98 | 69.9 | 0.268 | 0.025 | 42.54 | 9594 | 8.22 | 57 |  | 176.68 | 3.1 | 6.79 | -3.944 | 0.23 | 101
8/14/2025 03:15 | 10 | 19 | 2.75 | 7.735 | 7.286 | 7.09 | 55 | 1.98 | 69.9 | 0.268 | 0.025 | 42.54 | 9594 | 8.2 | 57 |  | 176.81 | 3.29 | 6.81 | -3.944 | 0.23 | 101
8/14/2025 03:30 | 11 | 19 | 2.75 | 8.123 | 3.135 | 7.1 | 55 | 1.98 | 69.9 | 0.268 | 0.025 | 42.54 | 9594 | 8.19 | 57 |  | 176.69 | 3.13 | 6.81 | -3.944 | 0.24 | 101
8/14/2025 03:45 | 11 | 19 | 2.75 | 8.497 | 2.76 | 7.1 | 55 | 1.98 | 69.9 | 0.268 | 0.025 | 42.54 | 9594 | 8.18 | 57 |  | 176.26 | 2.99 | 6.8 | -3.944 | 0.25 | 101
8/14/2025 04:00 | 10 | 19 | 2.75 | 8.459 | 2.579 | 7.1 | 55 | 1.98 | 69.9 | 0.295 | 0.025 | 42.54 | 9594 | 8.16 | 57 |  | 176.61 | 3.01 | 6.8 | -3.944 | 0.23 | 101
8/14/2025 04:15 | 8 | 19 | 2.75 | 8.498 | 2.663 | 7.1 | 55 | 1.98 | 69.9 | 0.295 | 0.025 | 42.54 | 9594 | 8.15 | 57 |  | 176.1 | 2.98 | 6.82 | -3.944 | 0.24 | 101
8/14/2025 04:30 | 11 | 19 | 2.75 | 7.778 | 2.532 | 7.1 | 55 | 1.98 | 69.9 | 0.295 | 0.025 | 42.54 | 9594 | 8.15 | 57 |  | 176.03 | 3.26 | 6.83 | -3.944 | 0.23 | 101
8/14/2025 04:45 | 12 | 19 | 2.75 | 7.799 | 3.014 | 7.09 | 55 | 1.98 | 69.9 | 0.295 | 0.025 | 42.54 | 9594 | 8.14 | 57 |  | 176.04 | 3.25 | 6.83 | -3.944 | 0.22 | 101
8/14/2025 05:00 | 9 | 19 | 2.75 | 8.135 | 2.964 | 7.09 | 55 | 1.98 | 69.9 | 0.295 | 0.025 | 42.54 | 9594 | 8.13 | 57 |  | 176.23 | 3.12 | 6.81 | -3.944 | 0.22 | 101
8/14/2025 05:15 | 10 | 19 | 2.75 | 8.31 | 2.91 | 7.09 | 55 | 1.98 | 69.9 | 0.295 | 0.025 | 42.54 | 9594 | 8.12 | 57 |  | 176.05 | 3.05 | 6.8 | -3.944 | 0.22 | 101
8/14/2025 05:30 | 5 | 19 | 2.75 | 8.342 | 2.968 | 7.09 | 55 | 1.98 | 69.9 | 0.295 | 0.025 | 42.54 | 9594 | 8.12 | 57 |  | 175.46 | 3.03 | 6.8 | -3.944 | 0.22 | 101
8/14/2025 05:45 | 10 | 19 | 2.75 | 8.315 | 2.878 | 7.09 | 55 | 1.98 | 69.9 | 0.295 | 0.025 | 42.54 | 9594 | 8.11 | 57 |  | 175.8 | 3.04 | 6.8 | -3.944 | 0.22 | 101
8/14/2025 06:00 | 11 | 19 | 2.75 | 8.327 | 2.89 | 7.09 | 55 | 1.98 | 69.9 | 0.295 | 0.025 | 42.54 | 9594 | 8.11 | 57 |  | 175.79 | 3.04 | 6.79 | -3.944 | 0.22 | 101
8/14/2025 06:15 | 9 | 19 | 2.75 | 7.817 | 2.885 | 7.08 | 55 | 1.98 | 69.9 | 0.295 | 0.025 | 42.54 | 9594 | 8.1 | 57 |  | 175.54 | 3.23 | 6.8 | -3.944 | 0.22 | 101
8/14/2025 06:30 | 11 | 19 | 2.75 | 7.891 | 3.093 | 7.07 | 55 | 1.98 | 69.9 | 0.295 | 0.025 | 42.54 | 9594 | 8.1 | 57 |  | 175.65 | 3.21 | 6.8 | -3.944 | 0.23 | 101
8/14/2025 06:45 | 9 | 19 | 2.75 | 8.136 | 3.003 | 7.08 | 55 | 1.98 | 69.9 | 0.295 | 0.024 | 42.54 | 9594 | 8.09 | 57 |  | 175.55 | 3.11 | 6.8 | -3.944 | 0.23 | 101
8/14/2025 07:00 | 10 | 19 | 2.75 | 8.176 | 3.076 | 7.08 | 55 | 1.98 | 69.9 | 0.295 | 0.024 | 42.54 | 9594 | 8.09 | 57 |  | 175.49 | 3.09 | 6.81 | -3.944 | 0.22 | 101
8/14/2025 07:15 | 8 | 19 | 2.75 | 8.203 | 3.033 | 7.09 | 55 | 1.98 | 69.9 | 0.295 | 0.024 | 42.54 | 9594 | 8.08 | 57 |  | 175.85 | 3.09 | 6.81 | -3.944 | 0.22 | 101
8/14/2025 07:30 | 7 | 19 | 2.75 | 8.224 | 3.038 | 7.09 | 55 | 1.98 | 69.9 | 0.295 | 0.024 | 42.54 | 9594 | 8.08 | 57 |  | 175.3 | 3.07 | 6.82 | -3.944 | 0.22 | 101
8/14/2025 07:45 | 11 | 19 | 2.75 | 8.212 | 3.066 | 7.1 | 55 | 1.98 | 69.9 | 0.295 | 0.024 | 42.54 | 9594 | 8.08 | 57 |  | 175.58 | 3.08 | 6.83 | -3.944 | 0.24 | 101
8/14/2025 08:00 | 10 | 19 | 2.75 | 8.178 | 2.889 | 7.1 | 55 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.08 | 57 |  | 175.08 | 3.08 | 6.83 | -3.944 | 0.22 | 101
8/14/2025 08:15 | 7 | 19 | 2.75 | 7.995 | 2.847 | 7.11 | 55 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.08 | 57 |  | 175.15 | 3.15 | 6.84 | -3.944 | 0.22 | 101
8/14/2025 08:30 | 5 | 19 | 2.75 | 8.31 | 2.904 | 7.11 | 55 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.07 | 57 |  | 174.98 | 3.03 | 6.84 | -3.944 | 0.22 | 101
8/14/2025 08:45 | 8 | 19 | 2.75 | 8.313 | 2.772 | 7.11 | 55 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.07 | 57 |  | 175.34 | 3.04 | 6.83 | -3.944 | 0.22 | 101
8/14/2025 09:00 | 10 | 19 | 2.75 | 8.325 | 2.856 | 7.11 | 55 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.07 | 57 |  | 174.98 | 3.03 | 6.83 | -3.944 | 0.22 | 101
8/14/2025 09:15 | 8 | 19 | 2.75 | 8.272 | 2.846 | 7.11 | 55 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.06 | 57 |  | 174.79 | 3.04 | 6.83 | -3.944 | 0.22 | 101
8/14/2025 09:30 | 11 | 19 | 2.75 | 8.277 | 2.816 | 7.11 | 55 | 1.98 | 69.9 | 0.274 | 0.023 | 42.54 | 9594 | 8.06 | 57 |  | 175.13 | 3.05 | 6.83 | -3.944 | 0.22 | 101
8/14/2025 09:45 | 12 | 19 | 2.75 | 8.764 | 2.999 | 7.11 | 55 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.05 | 57 |  | 175.15 | 2.88 | 6.83 | -3.944 | 0.24 | 101
8/14/2025 10:00 | 6 | 19 | 2.75 | 9.212 | 2.963 | 7.11 | 52 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.05 | 57 |  | 175.17 | 2.74 | 6.82 | -3.944 | 0.22 | 101
8/14/2025 10:15 | 11 | 19 | 2.75 | 9.268 | 3.015 | 7.11 | 52 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.07 | 57 |  | 175.65 | 2.73 | 6.82 | -3.944 | 0.23 | 101
8/14/2025 10:30 | 11 | 19 | 2.75 | 9.25 | 2.995 | 7.11 | 52 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.09 | 57 |  | 175.36 | 2.73 | 6.82 | -3.944 | 0.25 | 101
8/14/2025 10:45 | 6 | 19 | 2.75 | 9.287 | 3.009 | 7.11 | 52 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.1 | 57 |  | 175.01 | 2.71 | 6.82 | -3.944 | 0.23 | 101
8/14/2025 11:00 | 10 | 19 | 2.75 | 9.272 | 3.02 | 7.11 | 52 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.11 | 57 |  | 175.5 | 2.73 | 6.82 | -3.944 | 0.29 | 101
8/14/2025 11:15 | 7 | 19 | 2.75 | 9.293 | 3.058 | 7.11 | 52 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.11 | 57 |  | 175.59 | 2.72 | 6.82 | -3.944 | 0.22 | 101
8/14/2025 11:30 | 6 | 19 | 2.75 | 9.334 | 39.935 | 7.11 | 52 | 1.98 | 69.9 | 0.274 | 0.024 | 42.54 | 9594 | 8.12 | 57 |  | 175.6 | 2.71 | 6.75 | -3.944 | 0.27 | 101
8/14/2025 11:45 | 10 | 19 | 2.75 | 9.272 | 2.479 | 7.08 | 52 | 1.98 | 69.9 | 0.274 | 0.023 | 42.54 | 9594 | 8.13 | 57 |  | 175.12 | 2.72 | 6.75 | -3.944 | 0.25 | 101
8/14/2025 12:00 | 14 | 19 | 2.75 | 9.206 | 2.416 | 7.11 | 52 | 1.98 | 69.9 | 0.18 | 0.023 | 42.54 | 9594 | 8.13 | 57 |  | 176.29 | 2.76 | 6.83 | -3.944 | 0.25 | 100
8/14/2025 12:15 | 16 | 19 | 2.75 | 8.889 | 2.361 | 7.13 | 52 | 1.98 | 69.9 | 0.18 | 0.023 | 42.54 | 9594 | 8.12 | 57 |  | 198.53 | 3.22 | 6.85 | -3.944 | 0.23 | 99
8/14/2025 12:30 | 15 | 19 | 2.75 | 9.11 | 3.949 | 7.13 | 52 | 1.98 | 69.9 | 0.18 | 0.023 | 42.54 | 9594 | 8.12 | 57 |  | 179.96 | 2.84 | 6.84 | -3.944 | 0.24 | 99
8/14/2025 12:45 | 15 | 19 | 2.75 | 9.099 | 2.562 | 7.13 | 52 | 1.98 | 69.9 | 0.18 | 0.023 | 42.54 | 9594 | 8.12 | 57 |  | 179.95 | 2.85 | 6.84 | -3.944 | 0.26 | 99
8/14/2025 13:00 | 15 | 19 | 2.75 | 9.098 | 2.24 | 7.14 | 52 | 1.98 | 69.9 | 0.18 | 0.023 | 42.54 | 9594 | 8.11 | 57 |  | 180.22 | 2.85 | 6.85 | -3.944 | 0.26 | 99
8/14/2025 13:15 | 12 | 19 | 2.75 | 9.121 | 2.161 | 7.14 | 52 | 1.98 | 69.9 | 0.18 | 0.023 | 42.54 | 9594 | 8.1 | 57 |  | 180.49 | 2.85 | 6.86 | -3.944 | 0.24 | 101
8/14/2025 13:30 | 15 | 19 | 2.75 | 9.151 | 2.087 | 7.15 | 52 | 1.98 | 69.9 | 0.18 | 0.023 | 42.54 | 9594 | 8.1 | 57 |  | 180.19 | 2.84 | 6.86 | -3.944 | 0.25 | 99
8/14/2025 13:45 | 14 | 19 | 2.75 | 9.075 | 2.042 | 7.15 | 52 | 1.98 | 69.9 | 0.18 | 0.023 | 42.54 | 9594 | 8.1 | 57 |  | 179.86 | 2.85 | 6.86 | -3.944 | 0.25 | 99
8/14/2025 14:00 | 15 | 19 | 2.75 | 9.038 | 2.059 | 7.15 | 52 | 1.98 | 70.3 | 0.18 | 0.023 | 42.54 | 9594 | 8.1 | 58 |  | 180.53 | 2.88 | 6.85 | -3.944 | 0.26 | 99
8/14/2025 14:15 | 14 | 19 | 2.75 | 9.058 | 2.79 | 7.11 | 52 | 1.98 | 70.3 | 0.18 | 0.023 | 42.54 | 9594 | 8.1 | 58 |  | 179.85 | 2.86 | 6.8 | -3.944 | 0.22 | 99
8/14/2025 14:30 | 13 | 19 | 2.75 | 9.098 | 2.9 | 7.1 | 52 | 1.98 | 70.3 | 0.18 | 0.023 | 42.54 | 9594 | 8.09 | 58 |  | 180.25 | 2.85 | 6.8 | -3.944 | 0.24 | 99
8/14/2025 14:45 | 9 | 19 | 2.75 | 9.032 | 2.63 | 7.12 | 52 | 1.98 | 70.3 | 0.18 | 0.023 | 42.54 | 9594 | 8.08 | 58 |  | 180.32 | 2.87 | 6.82 | -3.944 | 0.24 | 101
8/14/2025 15:00 | 13 | 19 | 2.75 | 9.098 | 2.831 | 7.1 | 52 | 1.98 | 70.3 | 0.18 | 0.023 | 42.54 | 9594 | 8.08 | 58 |  | 180.17 | 2.85 | 6.8 | -3.944 | 0.24 | 101
8/14/2025 15:15 | 15 | 19 | 2.75 | 8.606 | 2.587 | 7.11 | 52 | 1.98 | 70.3 | 0.18 | 0.023 | 42.54 | 9594 | 8.07 | 58 |  | 180.53 | 3.02 | 6.82 | -3.944 | 0.27 | 99
8/14/2025 15:30 | 12 | 19 | 2.75 | 8.971 | 2.503 | 7.12 | 52 | 1.98 | 70.3 | 0.18 | 0.022 | 42.54 | 9594 | 8.06 | 58 |  | 180.79 | 2.9 | 6.83 | -3.944 | 0.26 | 101
8/14/2025 15:45 | 16 | 19 | 2.75 | 8.973 | 2.57 | 7.12 | 52 | 1.98 | 70.3 | 0.18 | 0.023 | 42.54 | 9594 | 8.06 | 58 |  | 180.1 | 2.89 | 6.82 | -3.944 | 0.25 | 99
8/14/2025 16:00 | 14 | 19 | 2.75 | 9.015 | 2.581 | 7.12 | 52 | 1.98 | 70.3 | 0.206 | 0.023 | 42.54 | 9594 | 8.06 | 58 |  | 180.25 | 2.88 | 6.82 | -3.944 | 0.25 | 99
8/14/2025 16:15 | 17 | 19 | 2.75 | 7.646 | 2.472 | 7.12 | 52 | 1.98 | 70.3 | 0.206 | 0.023 | 41.82 | 9494 | 8.05 | 58 |  | 180.61 | 3.4 | 6.83 | -3.944 | 0.24 | 99
8/14/2025 16:30 | 19 | 19 | 2.75 | 8.202 | 2.415 | 7.12 | 52 | 1.98 | 70.3 | 0.206 | 0.023 | 41.82 | 9494 | 8.06 | 58 |  | 180.21 | 3.16 | 6.83 | -3.944 | 0.25 | 99
8/14/2025 16:45 | 19 | 19 | 2.75 | 8.243 | 2.469 | 7.12 | 52 | 1.98 | 70.3 | 0.206 | 0.023 | 41.82 | 9494 | 8.06 | 58 |  | 179.75 | 3.14 | 6.82 | -3.944 | 0.25 | 99
8/14/2025 17:00 | 19 | 19 | 2.75 | 7.427 | 2.394 | 7.13 | 52 | 1.98 | 70.3 | 0.206 | 0.023 | 41.82 | 9494 | 8.07 | 58 |  | 179.35 | 3.48 | 6.83 | -3.944 | 0.24 | 99
8/14/2025 17:15 | 19 | 19 | 2.75 | 7.39 | 2.675 | 7.13 | 52 | 1.98 | 70.3 | 0.206 | 0.023 | 41.82 | 9494 | 8.07 | 58 |  | 179.32 | 3.49 | 6.83 | -3.944 | 0.24 | 100
8/14/2025 17:30 | 20 | 19 | 2.75 | 7.588 | 2.64 | 7.13 | 52 | 1.98 | 70.3 | 0.206 | 0.023 | 41.82 | 9494 | 8.06 | 58 |  | 179.89 | 3.41 | 6.83 | -3.944 | 0.23 | 99
8/14/2025 17:45 | 18 | 19 | 2.75 | 7.645 | 2.427 | 7.14 | 52 | 1.98 | 70.3 | 0.206 | 0.023 | 41.82 | 9494 | 8.05 | 58 |  | 180.05 | 3.39 | 6.83 | -3.944 | 0.25 | 99
8/14/2025 18:00 | 20 | 19 | 2.75 | 7.612 | 2.311 | 7.16 | 52 | 1.98 | 70.5 | 0.206 | 0.023 | 41.82 | 9494 | 8.06 | 58 |  | 179.74 | 3.4 | 6.85 | -3.944 | 0.24 | 100
8/14/2025 18:15 | 18 | 19 | 2.75 | 5.547 | 2.337 | 7.15 | 52 | 1.98 | 70.5 | 0.206 | 0.023 | 38.95 | 8215 | 8.08 | 58 |  | 135.91 | 3.53 | 6.84 | -3.944 | 0.23 | 99
8/14/2025 18:30 | 23 | 19 | 2.75 | 4.791 | 2.215 | 7.15 | 52 | 1.98 | 70.5 | 0.206 | 0.023 | 38.95 | 8215 | 8.11 | 58 |  | 116.11 | 3.49 | 6.84 | -3.944 | 0.22 | 100
8/14/2025 18:45 | 21 | 19 | 2.75 | 4.422 | 2.366 | 7.16 | 52 | 1.98 | 70.5 | 0.206 | 0.023 | 38.95 | 8215 | 8.14 | 58 |  | 107.78 | 3.51 | 6.86 | -3.944 | 0.22 | 100
8/14/2025 19:00 | 20 | 19 | 2.75 | 4.522 | 2.542 | 7.15 | 52 | 1.98 | 70.5 | 0.206 | 0.023 | 38.95 | 8215 | 8.17 | 58 |  | 109.42 | 3.48 | 6.84 | -3.944 | 0.23 | 100
8/14/2025 19:15 | 20 | 19 | 2.75 | 7.409 | 2.352 | 7.16 | 52 | 1.98 | 70.5 | 0.206 | 0.023 | 38.95 | 8215 | 8.19 | 58 |  | 179.65 | 3.49 | 6.83 | -3.944 | 0.24 | 100
8/14/2025 19:30 | 14 | 19 | 2.75 | 7.387 | 2.231 | 7.17 | 52 | 1.98 | 70.5 | 0.206 | 0.023 | 38.95 | 8215 | 8.2 | 58 |  | 178.77 | 3.48 | 6.84 | -3.944 | 0.24 | 100
8/14/2025 19:45 | 12 | 19 | 2.75 | 7.325 | 2.417 | 7.17 | 52 | 1.98 | 70.5 | 0.206 | 0.023 | 38.95 | 8215 | 8.23 | 58 |  | 179.2 | 3.52 | 6.83 | -3.944 | 0.24 | 101
8/14/2025 20:00 | 16 | 19 | 2.75 | 6.674 | 2.412 | 7.17 | 52 | 1.98 | 70.5 | 0.288 | 0.024 | 38.95 | 8215 | 8.25 | 58 |  | 0 | 0 | 6.83 | -3.944 | 0.23 | 100
8/14/2025 20:15 | 14 | 19 | 2.75 | 6.415 | 2.852 | 7.21 | 52 | 1.98 | 70.5 | 0.288 | 0.024 | 38.95 | 8215 | 8.25 | 58 |  | 0 | 0 | 6.83 | -3.944 | 0.24 | 99
8/14/2025 20:30 | 13 | 19 | 2.75 | 6.788 | 3.262 | 7.19 | 52 | 1.98 | 70.5 | 0.288 | 0.023 | 38.95 | 8215 | 8.22 | 58 |  | 0 | 0 | 6.82 | -3.944 | 0.23 | 101
8/14/2025 20:45 | 13 | 19 | 2.75 | 6.939 | 2.94 | 7.21 | 52 | 1.98 | 70.5 | 0.288 | 0.023 | 38.95 | 8215 | 8.22 | 58 |  | 0 | 0 | 6.83 | -3.944 | 0.25 | 101
8/14/2025 21:00 | 14 | 19 | 2.75 | 7.055 | 2.73 | 7.22 | 52 | 1.98 | 70.5 | 0.288 | 0.023 | 38.95 | 8215 | 8.24 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.25 | 100
8/14/2025 21:15 | 11 | 19 | 2.75 | 6.992 | 3.334 | 7.22 | 52 | 1.98 | 70.5 | 0.288 | 0.023 | 38.95 | 8215 | 8.26 | 58 |  | 0 | 0 | 6.86 | -3.944 | 0.22 | 101
8/14/2025 21:30 | 11 | 19 | 2.75 | 6.21 | 4.5 | 7.15 | 52 | 1.98 | 70.5 | 0.288 | 0.024 | 38.44 | 8236 | 8.27 | 58 |  | 0 | 0 | 6.79 | -3.944 | 0.2 | 101
8/14/2025 21:45 | 12 | 19 | 2.75 | 6.19 | 4.535 | 7.16 | 52 | 1.98 | 70.5 | 0.288 | 0.025 | 38.44 | 8236 | 8.27 | 58 |  | 0 | 0 | 6.8 | -3.944 | 0.23 | 101
8/14/2025 22:00 | 9 | 19 | 2.75 | 6.743 | 4.235 | 7.18 | 53 | 1.98 | 70.3 | 0.288 | 0.025 | 38.44 | 8236 | 8.27 | 58 |  | 0 | 0 | 6.82 | -3.944 | 0.24 | 101
8/14/2025 22:15 | 7 | 19 | 2.75 | 6.742 | 4.026 | 7.19 | 53 | 1.98 | 70.3 | 0.288 | 0.025 | 38.44 | 8236 | 8.25 | 58 |  | 0 | 0 | 6.83 | -3.944 | 0.24 | 101
8/14/2025 22:30 | 12 | 19 | 2.75 | 6.727 | 3.774 | 7.2 | 53 | 1.98 | 70.3 | 0.288 | 0.025 | 38.44 | 8236 | 8.22 | 58 |  | 0 | 0 | 6.84 | -3.944 | 0.23 | 101
8/14/2025 22:45 | 12 | 19 | 2.75 | 6.708 | 3.957 | 7.19 | 53 | 1.98 | 70.3 | 0.288 | 0.025 | 38.44 | 8236 | 8.24 | 58 |  | 0 | 0 | 6.84 | -3.944 | 0.23 | 101
8/14/2025 23:00 | 13 | 19 | 2.75 | 6.29 | 3.799 | 7.19 | 53 | 1.98 | 70.3 | 0.288 | 0.025 | 38.44 | 8236 | 8.27 | 58 |  | 0 | 0 | 6.84 | -3.944 | 0.24 | 100
8/14/2025 23:15 | 13 | 19 | 2.75 | 6.294 | 3.626 | 7.2 | 53 | 1.98 | 70.3 | 0.288 | 0.025 | 38.44 | 8236 | 8.3 | 58 |  | 0 | 0 | 6.84 | -3.944 | 0.23 | 101
8/14/2025 23:30 | 10 | 19 | 2.75 | 6.582 | 3.543 | 7.21 | 53 | 1.98 | 70.3 | 0.288 | 0.024 | 38.44 | 8236 | 8.31 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.24 | 101
8/14/2025 23:45 | 8 | 19 | 2.75 | 6.793 | 3.736 | 7.19 | 53 | 1.98 | 70.3 | 0.288 | 0.024 | 38.44 | 8236 | 8.32 | 58 |  | 0 | 0 | 6.84 | -3.944 | 0.3 | 101
8/15/2025 00:00 | 9 | 19 | 2.75 | 6.751 | 3.576 | 7.19 | 53 | 1.98 | 70.3 | 0.221 | 0.024 | 38.44 | 8236 | 8.32 | 58 |  | 0 | 0 | 6.84 | -3.944 | 0.25 | 101
8/15/2025 00:15 | 7 | 19 | 2.75 | 6.357 | 3.321 | 7.21 | 53 | 1.98 | 70.3 | 0.221 | 0.024 | 38.44 | 8236 | 8.32 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.25 | 101
8/15/2025 00:30 | 9 | 19 | 2.75 | 6.001 | 3.011 | 7.22 | 53 | 1.98 | 70.3 | 0.221 | 0.024 | 38.44 | 8236 | 8.32 | 58 |  | 0 | 0 | 6.86 | -3.944 | 0.25 | 101
8/15/2025 00:45 | 8 | 19 | 2.75 | 6.259 | 2.929 | 7.22 | 53 | 1.98 | 70.3 | 0.221 | 0.024 | 38.44 | 8236 | 8.32 | 58 |  | 0 | 0 | 6.86 | -3.944 | 0.25 | 101
8/15/2025 01:00 | 5 | 19 | 2.75 | 6.309 | 3.164 | 7.2 | 53 | 1.98 | 70.3 | 0.221 | 0.024 | 38.44 | 8236 | 8.31 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.23 | 101
8/15/2025 01:15 | 5 | 19 | 2.75 | 6.279 | 3.457 | 7.19 | 53 | 1.98 | 70.3 | 0.221 | 0.024 | 38.44 | 8236 | 8.31 | 58 |  | 0 | 0 | 6.83 | -3.944 | 0.23 | 101
8/15/2025 01:30 | 0 | 19 | 2.75 | 6.949 | 4.063 | 7.16 | 53 | 1.98 | 70.3 | 0.221 | 0.024 | 38.44 | 8236 | 8.31 | 58 |  | 0 | 0 | 6.8 | -3.944 | 0.23 | 101
8/15/2025 01:45 | 7 | 19 | 2.75 | 6.856 | 4.292 | 7.14 | 53 | 1.98 | 70.3 | 0.221 | 0.025 | 36.52 | 7897 | 8.31 | 58 |  | 0 | 0 | 6.79 | -3.944 | 0.22 | 101
8/15/2025 02:00 | 10 | 19 | 2.75 | 6.751 | 4.479 | 7.14 | 53 | 1.98 | 70.1 | 0.221 | 0.026 | 36.52 | 7897 | 8.31 | 58 |  | 0 | 0 | 6.79 | -3.944 | 0.22 | 101
8/15/2025 02:15 | 10 | 19 | 2.75 | 6.772 | 4.689 | 7.14 | 53 | 1.98 | 70.1 | 0.221 | 0.026 | 36.52 | 7897 | 8.3 | 58 |  | 0 | 0 | 6.8 | -3.944 | 0.22 | 101
8/15/2025 02:30 | 10 | 19 | 2.75 | 6.752 | 4.325 | 7.16 | 53 | 1.98 | 70.1 | 0.221 | 0.026 | 36.52 | 7897 | 8.29 | 58 |  | 0 | 0 | 6.81 | -3.944 | 0.23 | 101
8/15/2025 02:45 | 1 | 19 | 2.75 | 6.782 | 4.186 | 7.17 | 53 | 1.98 | 70.1 | 0.221 | 0.026 | 36.52 | 7897 | 8.25 | 58 |  | 0 | 0 | 6.83 | -3.944 | 0.23 | 101
8/15/2025 03:00 | 7 | 19 | 2.75 | 6.554 | 3.857 | 7.18 | 53 | 1.98 | 70.1 | 0.221 | 0.026 | 36.52 | 7897 | 8.23 | 58 |  | 0 | 0 | 6.84 | -3.944 | 0.24 | 101
8/15/2025 03:15 | 9 | 19 | 2.75 | 6.054 | 3.802 | 7.18 | 53 | 1.98 | 70.1 | 0.221 | 0.026 | 36.52 | 7897 | 8.25 | 58 |  | 0 | 0 | 6.86 | -3.944 | 0.23 | 101
8/15/2025 03:30 | 9 | 19 | 2.75 | 6.499 | 3.825 | 7.18 | 53 | 1.98 | 70.1 | 0.221 | 0.025 | 36.52 | 7897 | 8.28 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.24 | 101
8/15/2025 03:45 | 8 | 19 | 2.75 | 6.515 | 3.853 | 7.18 | 53 | 1.98 | 70.1 | 0.221 | 0.025 | 36.52 | 7897 | 8.3 | 58 |  | 0 | 0 | 6.83 | -3.944 | 0.23 | 101
8/15/2025 04:00 | 4 | 19 | 2.75 | 6.778 | 3.992 | 7.17 | 53 | 1.98 | 70.1 | 0.24 | 0.026 | 36.52 | 7897 | 8.3 | 58 |  | 0 | 0 | 6.82 | -3.944 | 0.23 | 101
8/15/2025 04:15 | -1 | 19 | 2.75 | 6.78 | 4.073 | 7.16 | 53 | 1.98 | 70.1 | 0.24 | 0.025 | 36.21 | 7884 | 8.3 | 58 |  | 0 | 0 | 6.81 | -3.944 | 0.24 | 101
8/15/2025 04:30 | 2 | 19 | 2.75 | 6.666 | 3.902 | 7.17 | 53 | 1.98 | 70.1 | 0.24 | 0.026 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.82 | -3.944 | 0.24 | 101
8/15/2025 04:45 | 9 | 19 | 2.75 | 8.327 | 3.828 | 7.18 | 53 | 1.98 | 70.1 | 0.24 | 0.027 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.83 | -3.944 | 0.25 | 101
8/15/2025 05:00 | 2 | 19 | 2.75 | 7.915 | 3.632 | 7.2 | 53 | 1.98 | 70.1 | 0.24 | 0.027 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.84 | -3.944 | 0.24 | 101
8/15/2025 05:15 | 6 | 19 | 2.75 | 8.051 | 3.612 | 7.2 | 53 | 1.98 | 70.1 | 0.24 | 0.027 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.84 | -3.944 | 0.25 | 101
8/15/2025 05:30 | 12 | 19 | 2.75 | 7.343 | 3.627 | 7.19 | 53 | 1.98 | 70.1 | 0.24 | 0.027 | 36.21 | 7884 | 8.3 | 58 |  | 0 | 0 | 6.83 | -3.944 | 0.24 | 101
8/15/2025 05:45 | 13 | 19 | 2.75 | 7.622 | 3.794 | 7.17 | 53 | 1.98 | 70.1 | 0.24 | 0.027 | 36.21 | 7884 | 8.31 | 58 |  | 0 | 0 | 6.82 | -3.944 | 0.22 | 101
8/15/2025 06:00 | 11 | 19 | 2.75 | 7.598 | 3.894 | 7.16 | 53 | 1.98 | 69.9 | 0.24 | 0.027 | 36.21 | 7884 | 8.31 | 58 |  | 0 | 0 | 6.82 | -3.944 | 0.23 | 101
8/15/2025 06:15 | 10 | 19 | 2.75 | 7.598 | 4.105 | 7.15 | 53 | 1.98 | 69.9 | 0.24 | 0.026 | 36.21 | 7884 | 8.31 | 58 |  | 0 | 0 | 6.81 | -3.944 | 0.23 | 101
8/15/2025 06:30 | 7 | 19 | 2.75 | 7.625 | 4.265 | 7.14 | 53 | 1.98 | 69.9 | 0.24 | 0.026 | 36.21 | 7884 | 8.3 | 58 |  | 0 | 0 | 6.8 | -3.944 | 0.22 | 101
8/15/2025 06:45 | 7 | 19 | 2.75 | 7.595 | 4.498 | 7.13 | 53 | 1.98 | 69.9 | 0.24 | 0.026 | 36.21 | 7884 | 8.3 | 58 |  | 0 | 0 | 6.79 | -3.944 | 0.22 | 101
8/15/2025 07:00 | 4 | 19 | 2.75 | 7.598 | 4.438 | 7.14 | 53 | 1.98 | 69.9 | 0.24 | 0.026 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.8 | -3.944 | 0.22 | 101
8/15/2025 07:15 | 5 | 19 | 2.75 | 7.569 | 4.581 | 7.14 | 53 | 1.98 | 69.9 | 0.24 | 0.026 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.81 | -3.944 | 0.21 | 101
8/15/2025 07:30 | 5 | 19 | 2.75 | 7.591 | 4.534 | 7.15 | 53 | 1.98 | 69.9 | 0.24 | 0.026 | 36.21 | 7884 | 8.3 | 58 |  | 0 | 0 | 6.81 | -3.944 | 0.21 | 101
8/15/2025 07:45 | 7 | 19 | 2.75 | 7.552 | 4.412 | 7.16 | 53 | 1.98 | 69.9 | 0.24 | 0.026 | 36.21 | 7884 | 8.28 | 58 |  | 0 | 0 | 6.82 | -3.944 | 0.21 | 101
8/15/2025 08:00 | 5 | 19 | 2.75 | 7.56 | 4.372 | 7.17 | 53 | 1.98 | 69.9 | 0.25 | 0.025 | 36.21 | 7884 | 8.27 | 58 |  | 0 | 0 | 6.84 | -3.944 | 0.22 | 101
8/15/2025 08:15 | 4 | 19 | 2.75 | 7.54 | 4.335 | 7.17 | 53 | 1.98 | 69.9 | 0.25 | 0.025 | 36.21 | 7884 | 8.27 | 58 |  | 0 | 0 | 6.81 | -3.944 | 0.38 | 101
8/15/2025 08:30 | 0 | 19 | 2.75 | 7.558 | 3.843 | 7.11 | 53 | 1.98 | 69.9 | 0.25 | 0.025 | 36.21 | 7884 | 8.27 | 58 |  | 0 | 0 | 6.75 | -3.944 | 0.22 | 101
8/15/2025 08:45 | 0 | 19 | 2.75 | 7.563 | 4.162 | 7.14 | 53 | 1.98 | 69.9 | 0.25 | 0.025 | 36.21 | 7884 | 8.27 | 58 |  | 0 | 0 | 6.77 | -3.944 | 0.21 | 101
8/15/2025 09:00 | -5 | 19 | 2.75 | 7.523 | 4.166 | 7.15 | 53 | 1.98 | 69.9 | 0.25 | 0.025 | 36.21 | 7884 | 8.27 | 58 |  | 0 | 0 | 6.83 | -3.944 | 0.23 | 101
8/15/2025 09:15 | 4 | 19 | 2.75 | 7.56 | 4.094 | 7.16 | 53 | 1.98 | 69.9 | 0.25 | 0.025 | 36.21 | 7884 | 8.28 | 58 |  | 0 | 0 | 6.84 | -3.944 | 0.22 | 101
8/15/2025 09:30 | 6 | 19 | 2.75 | 7.466 | 4.037 | 7.17 | 53 | 1.98 | 69.9 | 0.25 | 0.025 | 36.21 | 7884 | 8.27 | 58 |  | 0 | 0 | 6.84 | -3.944 | 0.24 | 101
8/15/2025 09:45 | 6 | 19 | 2.75 | 7.071 | 3.896 | 7.18 | 53 | 1.98 | 69.9 | 0.25 | 0.025 | 36.21 | 7884 | 8.27 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.24 | 101
8/15/2025 10:00 | 4 | 19 | 2.75 | 7.4 | 3.623 | 7.19 | 54 | 1.98 | 70.1 | 0.25 | 0.025 | 36.21 | 7884 | 8.27 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.24 | 101
8/15/2025 10:15 | 4 | 19 | 2.75 | 7.45 | 3.491 | 7.19 | 54 | 1.98 | 70.1 | 0.25 | 0.025 | 36.21 | 7884 | 8.27 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.24 | 101
8/15/2025 10:30 | 8 | 19 | 2.75 | 7.405 | 3.466 | 7.19 | 54 | 1.98 | 70.1 | 0.25 | 0.025 | 36.21 | 7884 | 8.27 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.24 | 101
8/15/2025 10:45 | 3 | 19 | 2.75 | 7.394 | 3.36 | 7.19 | 54 | 1.98 | 70.1 | 0.25 | 0.025 | 36.21 | 7884 | 8.27 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.24 | 101
8/15/2025 11:00 | 7 | 19 | 2.75 | 7.413 | 3.345 | 7.19 | 54 | 1.98 | 70.1 | 0.25 | 0.024 | 36.21 | 7884 | 8.28 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.24 | 101
8/15/2025 11:15 | 8 | 19 | 2.75 | 7.396 | 3.269 | 7.2 | 54 | 1.98 | 70.1 | 0.25 | 0.024 | 36.21 | 7884 | 8.28 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.24 | 101
8/15/2025 11:30 | 0 | 19 | 2.75 | 7.379 | 3.162 | 7.2 | 54 | 1.98 | 70.1 | 0.25 | 0.024 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.24 | 101
8/15/2025 11:45 | 4 | 19 | 2.75 | 7.331 | 3.101 | 7.21 | 54 | 1.98 | 70.1 | 0.25 | 0.024 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.85 | -3.944 | 0.24 | 101
8/15/2025 12:00 | 3 | 19 | 2.75 | 7.331 | 2.995 | 7.21 | 54 | 1.98 | 70.1 | 0.157 | 0.024 | 36.21 | 7884 | 8.3 | 58 |  | 0 | 0 | 6.85 | -3.852 | 0.24 | 101
8/15/2025 12:15 | 9 | 19 | 2.75 | 7.388 | 2.966 | 7.22 | 54 | 1.98 | 70.1 | 0.157 | 0.024 | 36.21 | 7884 | 8.3 | 58 |  | 0 | 0 | 6.85 | -3.852 | 0.23 | 101
8/15/2025 12:30 | 5 | 19 | 2.75 | 7.296 | 3.043 | 7.22 | 54 | 1.98 | 70.1 | 0.157 | 0.024 | 36.21 | 7884 | 8.3 | 58 |  | 0 | 0 | 6.85 | -3.852 | 0.23 | 101
8/15/2025 12:45 | 7 | 19 | 2.75 | 7.294 | 3.027 | 7.22 | 54 | 1.98 | 70.1 | 0.157 | 0.024 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.85 | -3.852 | 0.23 | 101
8/15/2025 13:00 | 7 | 19 | 2.75 | 7.354 | 3.008 | 7.23 | 54 | 1.98 | 70.1 | 0.157 | 0.024 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.86 | -3.852 | 0.24 | 101
8/15/2025 13:15 | 8 | 19 | 2.75 | 7.343 | 3.028 | 7.25 | 54 | 1.98 | 70.1 | 0.157 | 0.024 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.87 | -3.852 | 0.24 | 101
8/15/2025 13:30 | 5 | 19 | 2.75 | 7.326 | 2.955 | 7.25 | 54 | 1.98 | 70.1 | 0.157 | 0.024 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.87 | -3.852 | 0.24 | 101
8/15/2025 13:45 | 3 | 19 | 2.75 | 7.376 | 3.187 | 7.24 | 54 | 1.98 | 70.1 | 0.157 | 0.024 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.86 | -3.852 | 0.23 | 101
8/15/2025 14:00 | 6 | 19 | 2.75 | 7.259 | 3.336 | 7.22 | 54 | 1.98 | 70.3 | 0.157 | 0.024 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.86 | -3.852 | 0.22 | 101
8/15/2025 14:15 | 5 | 19 | 2.75 | 7.301 | 3.27 | 7.23 | 54 | 1.98 | 70.3 | 0.157 | 0.024 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.86 | -3.852 | 0.23 | 101
8/15/2025 14:30 | 5 | 19 | 2.75 | 7.353 | 3.694 | 7.21 | 54 | 1.98 | 70.3 | 0.157 | 0.024 | 36.21 | 7884 | 8.29 | 58 |  | 0 | 0 | 6.85 | -3.852 | 0.23 | 101
8/15/2025 14:45 | 3 | 19 | 2.75 | 7.314 | 3.782 | 7.21 | 54 | 1.98 | 70.3 | 0.157 | 0.024 | 36.21 | 7884 | 8.28 | 58 |  | 0 | 0 | 6.85 | -3.852 | 0.22 | 101
8/15/2025 15:00 | 3 | 19 | 2.75 | 7.306 | 3.758 | 7.21 | 54 | 1.98 | 70.3 | 0.157 | 0.024 | 36.21 | 7884 | 8.28 | 58 |  | 0 | 0 | 6.85 | -3.852 | 0.23 | 101
8/15/2025 15:15 | 0 | 19 | 2.75 | 7.344 | 3.783 | 7.22 | 54 | 1.98 | 70.3 | 0.157 | 0.024 | 36.21 | 7884 | 8.28 | 58 |  | 0 | 0 | 6.85 | -3.852 | 0.23 | 101
8/15/2025 15:30 | 4 | 19 | 2.75 | 7.355 | 3.611 | 7.24 | 54 | 1.98 | 70.3 | 0.157 | 0.024 | 36.21 | 7884 | 8.27 | 58 |  | 0 | 0 | 6.86 | -3.852 | 0.23 | 101
8/15/2025 15:45 | 3 | 19 | 2.75 | 7.318 | 3.399 | 7.26 | 54 | 1.98 | 70.3 | 0.157 | 0.024 | 36.21 | 7884 | 8.26 | 58 |  | 0 | 0 | 6.87 | -3.852 | 0.23 | 101
8/15/2025 16:00 | 4 | 19 | 2.75 | 7.156 | 3.474 | 7.28 | 54 | 1.98 | 70.3 | 0.145 | 0.024 | 36.21 | 7884 | 8.25 | 58 |  | 0 | 0 | 6.88 | -3.852 | 0.23 | 101
8/15/2025 16:15 | 3 | 19 | 2.75 | 6.864 | 3.752 | 7.26 | 54 | 1.98 | 70.3 | 0.145 | 0.024 | 36.57 | 8621 | 8.25 | 58 |  | 0 | 0 | 6.87 | -3.852 | 0.23 | 101
8/15/2025 16:30 | 4 | 19 | 2.75 | 7.332 | 3.817 | 7.25 | 54 | 1.98 | 70.3 | 0.145 | 0.025 | 36.57 | 8621 | 8.24 | 58 |  | 0 | 0 | 6.86 | -3.852 | 0.23 | 101
8/15/2025 16:45 | 4 | 19 | 2.75 | 7.33 | 4.279 | 7.24 | 54 | 1.98 | 70.3 | 0.145 | 0.026 | 36.57 | 8621 | 8.24 | 58 |  | 0 | 0 | 6.85 | -3.852 | 0.23 | 101
8/15/2025 17:00 | 3 | 19 | 2.75 | 7.352 | 4.109 | 7.23 | 54 | 1.98 | 70.3 | 0.145 | 0.026 | 36.57 | 8621 | 8.23 | 58 |  | 0 | 0 | 6.84 | -3.852 | 0.23 | 101
8/15/2025 17:15 | 4 | 19 | 2.75 | 7.3 | 3.989 | 7.23 | 54 | 1.98 | 70.3 | 0.145 | 0.026 | 36.57 | 8621 | 8.22 | 58 |  | 0 | 0 | 6.85 | -3.852 | 0.22 | 101
8/15/2025 17:30 | 5 | 19 | 2.75 | 7.291 | 4.141 | 7.21 | 54 | 1.98 | 70.3 | 0.145 | 0.026 | 36.57 | 8621 | 8.19 | 58 |  | 0 | 0 | 6.84 | -3.852 | 0.22 | 101
8/15/2025 17:45 | 5 | 19 | 2.75 | 7.541 | 4.38 | 7.19 | 54 | 1.98 | 70.3 | 0.145 | 0.026 | 36.57 | 8621 | 8.18 | 58 |  | 0 | 0 | 6.82 | -3.852 | 0.22 | 101
8/15/2025 18:00 | 6 | 19 | 2.75 | 7.56 | 4.138 | 7.2 | 54 | 1.98 | 70.5 | 0.145 | 0.025 | 36.57 | 8621 | 8.2 | 58 |  | 0 | 0 | 6.83 | -3.852 | 0.23 | 101
8/15/2025 18:15 | 7 | 19 | 2.75 | 7.579 | 4.165 | 7.2 | 54 | 1.98 | 70.5 | 0.145 | 0.025 | 36.57 | 8621 | 8.22 | 58 |  | 0 | 0 | 6.83 | -3.852 | 0.22 | 101
8/15/2025 18:30 | 9 | 19 | 2.75 | 7.611 | 3.991 | 7.21 | 54 | 1.98 | 70.5 | 0.145 | 0.025 | 36.57 | 8621 | 8.23 | 58 |  | 0 | 0 | 6.84 | -3.852 | 0.23 | 101
8/15/2025 18:45 | 8 | 19 | 2.75 | 7.574 | 4.307 | 7.2 | 54 | 1.98 | 70.5 | 0.145 | 0.025 | 36.57 | 8621 | 8.23 | 58 |  | 0 | 0 | 6.83 | -3.852 | 0.22 | 101
8/15/2025 19:00 | 9 | 19 | 2.75 | 7.535 | 3.943 | 7.22 | 54 | 1.98 | 70.5 | 0.145 | 0.025 | 36.57 | 8621 | 8.23 | 58 |  | 0 | 0 | 6.84 | -3.852 | 0.23 | 101
8/15/2025 19:15 | 8 | 19 | 2.75 | 7.53 | 4.138 | 7.22 | 54 | 1.98 | 70.5 | 0.145 | 0.025 | 36.57 | 8621 | 8.23 | 58 |  | 0 | 0 | 6.84 | -3.852 | 0.23 | 101
8/15/2025 19:30 | 8 | 19 | 2.75 | 7.576 | 4.016 | 7.21 | 54 | 1.98 | 70.5 | 0.145 | 0.025 | 36.57 | 8621 | 8.23 | 58 |  | 0 | 0 | 6.84 | -3.852 | 0.24 | 101
8/15/2025 19:45 | 8 | 19 | 2.75 | 7.506 | 4.122 | 7.2 | 54 | 1.98 | 70.5 | 0.145 | 0.025 | 36.57 | 8621 | 8.24 | 58 |  | 0 | 0 | 6.84 | -3.852 | 0.23 | 101
8/15/2025 20:00 | 9 | 19 | 2.75 | 7.514 | 4.077 | 7.2 | 54 | 1.98 | 70.5 | 0.173 | 0.025 | 36.57 | 8621 | 8.24 | 58 |  | 0 | 0 | 6.83 | -3.852 | 0.23 | 101
8/15/2025 20:15 | 10 | 19 | 2.75 | 7.549 | 3.997 | 7.2 | 54 | 1.98 | 70.5 | 0.173 | 0.025 | 36.57 | 8621 | 8.24 | 58 |  | 0 | 0 | 6.83 | -3.852 | 0.24 | 101
8/15/2025 20:30 | 10 | 19 | 2.75 | 7.601 | 3.894 | 7.22 | 54 | 1.98 | 70.5 | 0.173 | 0.025 | 36.57 | 8621 | 8.23 | 58 |  | 0 | 0 | 6.84 | -3.852 | 0.23 | 101
8/15/2025 20:45 | 9 | 19 | 2.75 | 7.526 | 3.788 | 7.21 | 54 | 1.98 | 70.5 | 0.173 | 0.025 | 36.57 | 8621 | 8.23 | 58 |  | 0 | 0 | 6.84 | -3.852 | 0.24 | 101
8/15/2025 21:00 | 9 | 19 | 2.75 | 6.994 | 3.869 | 7.19 | 54 | 1.98 | 70.5 | 0.173 | 0.025 | 36.57 | 8621 | 8.22 | 58 |  | 0 | 0 | 6.82 | -3.852 | 0.24 | 101
8/15/2025 21:15 | 9 | 19 | 2.75 | 7.096 | 4.046 | 7.15 | 54 | 1.98 | 70.5 | 0.173 | 0.025 | 36.57 | 8621 | 8.21 | 58 |  | 98.26 | 1.99 | 6.8 | -3.852 | 0.22 | 101
8/15/2025 21:30 | 9 | 19 | 2.75 | 7.638 | 5.013 | 7.13 | 54 | 1.98 | 70.5 | 0.173 | 0.025 | 36.57 | 8621 | 8.2 | 58 |  | 105.99 | 2 | 6.8 | -3.852 | 0.21 | 101
8/15/2025 21:45 | 10 | 19 | 2.75 | 8.714 | 3.633 | 7.14 | 54 | 1.98 | 70.5 | 0.173 | 0.025 | 36.57 | 8621 | 8.2 | 58 |  | 120.9 | 2 | 6.82 | -3.852 | 0.23 | 101
8/15/2025 22:00 | 9 | 19 | 2.75 | 8.757 | 22.665 | 7.15 | 55 | 1.98 | 70.7 | 0.173 | 0.025 | 36.57 | 8621 | 8.2 | 58 |  | 121.68 | 2 | 6.83 | -3.852 | 0.24 | 101
8/15/2025 22:15 | 10 | 19 | 2.75 | 8.76 | 39.937 | 7.13 | 55 | 1.98 | 70.7 | 0.173 | 0.026 | 36.57 | 8621 | 8.21 | 58 |  | 121.7 | 2 | 6.83 | -3.852 | 0.16 | 101
8/15/2025 22:30 | 12 | 19 | 2.75 | 8.748 | 14.946 | 7.14 | 55 | 1.98 | 70.7 | 0.173 | 0.026 | 36.57 | 8621 | 8.21 | 58 |  | 121.25 | 2 | 6.83 | -3.852 | 0.12 | 101
8/15/2025 22:45 | 11 | 19 | 2.75 | 8.711 | 6.575 | 7.16 | 55 | 1.98 | 70.7 | 0.173 | 0.026 | 36.57 | 8621 | 8.21 | 58 |  | 0 | 0 | 6.83 | -3.852 | 0.24 | 101
8/15/2025 23:00 | 10 | 19 | 2.75 | 8.705 | 4.921 | 7.17 | 55 | 1.98 | 70.7 | 0.173 | 0.026 | 36.57 | 8621 | 8.24 | 58 |  | 0 | 0 | 6.82 | -3.852 | 0.24 | 101
8/15/2025 23:15 | 8 | 19 | 2.75 | 9.325 | 4.22 | 7.16 | 55 | 1.98 | 70.7 | 0.173 | 0.026 | 36.57 | 8621 | 8.31 | 58 |  | 0 | 0 | 6.82 | -3.852 | 0.24 | 101
8/15/2025 23:30 | 8 | 19 | 2.75 | 8.725 | 3.532 | 7.13 | 55 | 1.98 | 70.7 | 0.173 | 0.025 | 36.57 | 8621 | 8.35 | 58 |  | 121.47 | 2 | 6.81 | -3.852 | 0.22 | 101
8/15/2025 23:45 | 9 | 19 | 2.75 | 8.744 | 3.211 | 7.13 | 55 | 1.98 | 70.7 | 0.173 | 0.025 | 36.57 | 8621 | 8.36 | 58 |  | 122.16 | 2.01 | 6.81 | -3.852 | 0.23 | 101
8/16/2025 00:00 | 9 | 19 | 2.75 | 8.757 | 3.075 | 7.12 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.34 | 58 |  | 121.88 | 2 | 6.81 | -3.852 | 0.22 | 101
8/16/2025 00:15 | 10 | 19 | 2.75 | 8.812 | 3.091 | 7.13 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.32 | 58 |  | 121.59 | 1.99 | 6.81 | -3.852 | 0.23 | 101
8/16/2025 00:30 | 9 | 19 | 2.75 | 9.112 | 3.258 | 7.13 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.29 | 58 |  | 126.74 | 2 | 6.82 | -3.852 | 0.23 | 101
8/16/2025 00:45 | 9 | 19 | 2.75 | 9.109 | 3.477 | 7.13 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.27 | 58 |  | 158.23 | 2.5 | 6.82 | -3.852 | 0.23 | 101
8/16/2025 01:00 | 10 | 19 | 2.75 | 9.12 | 3.269 | 7.12 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.25 | 58 |  | 157.08 | 2.48 | 6.82 | -3.852 | 0.24 | 101
8/16/2025 01:15 | 10 | 19 | 2.75 | 9.102 | 3.709 | 7.13 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.23 | 58 |  | 95.62 | 1.51 | 6.82 | -3.852 | 0.22 | 101
8/16/2025 01:30 | 8 | 19 | 2.75 | 9.089 | 3.529 | 7.13 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.22 | 58 |  | 94.37 | 1.5 | 6.81 | -3.852 | 0.24 | 101
8/16/2025 01:45 | 10 | 19 | 2.75 | 8.264 | 3.097 | 7.13 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.2 | 58 |  | 86.3 | 1.5 | 6.81 | -3.852 | 0.27 | 101
8/16/2025 02:00 | 11 | 19 | 2.75 | 8.212 | 3.264 | 7.12 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.19 | 58 |  | 86.23 | 1.51 | 6.8 | -3.852 | 0.22 | 101
8/16/2025 02:15 | 2 | 19 | 2.75 | 8.586 | 3.135 | 7.12 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.19 | 58 |  | 88.92 | 1.49 | 6.8 | -3.852 | 0.23 | 101
8/16/2025 02:30 | 8 | 19 | 2.75 | 8.529 | 3.263 | 7.13 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.18 | 58 |  | 88.68 | 1.5 | 6.8 | -3.852 | 0.24 | 101
8/16/2025 02:45 | 9 | 19 | 2.75 | 8.602 | 3.367 | 7.12 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.18 | 58 |  | 89.4 | 1.5 | 6.8 | -3.852 | 0.22 | 101
8/16/2025 03:00 | 8 | 19 | 2.75 | 8.578 | 3.259 | 7.13 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.18 | 58 |  | 165.87 | 2.78 | 6.8 | -3.852 | 0.23 | 101
8/16/2025 03:15 | 9 | 19 | 2.75 | 8.5 | 2.808 | 7.12 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.18 | 58 |  | 177.28 | 3 | 6.81 | -3.852 | 0.23 | 101
8/16/2025 03:30 | 11 | 19 | 2.75 | 8.478 | 5.359 | 7.12 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.18 | 58 |  | 177.48 | 3.01 | 6.82 | -3.852 | 0.23 | 101
8/16/2025 03:45 | 10 | 19 | 2.75 | 9.776 | 3.238 | 7.12 | 55 | 1.98 | 70.7 | 0.189 | 0.025 | 36.57 | 8621 | 8.18 | 58 |  | 179.29 | 2.64 | 6.82 | -3.852 | 0.27 | 101
8/16/2025 04:00 | 10 | 19 | 2.75 | 9.246 | 2.866 | 7.12 | 55 | 1.98 | 70.7 | 0.338 | 0.025 | 36.57 | 8621 | 8.18 | 58 |  | 179.59 | 2.8 | 6.82 | -3.852 | 0.23 | 101
8/16/2025 04:15 | 9 | 19 | 2.75 | 9.527 | 2.791 | 7.11 | 55 | 1.98 | 70.7 | 0.338 | 0.025 | 36.57 | 8621 | 8.18 | 58 |  | 179.84 | 2.72 | 6.82 | -3.852 | 0.25 | 101
8/16/2025 04:30 | 11 | 19 | 2.75 | 9.53 | 2.757 | 7.11 | 55 | 1.98 | 70.7 | 0.338 | 0.025 | 36.57 | 8621 | 8.17 | 58 |  | 179.03 | 2.71 | 6.81 | -3.852 | 0.24 | 101
8/16/2025 04:45 | 7 | 19 | 2.75 | 9.558 | 2.655 | 7.1 | 55 | 1.98 | 70.7 | 0.338 | 0.025 | 36.57 | 8621 | 8.18 | 58 |  | 179.86 | 2.71 | 6.81 | -3.852 | 0.24 | 101
8/16/2025 05:00 | 9 | 19 | 2.75 | 8.112 | 2.861 | 7.09 | 55 | 1.98 | 70.7 | 0.338 | 0.025 | 35.23 | 8488 | 8.21 | 58 |  | 169.34 | 3.01 | 6.81 | -3.852 | 0.22 | 101
8/16/2025 05:15 | 9 | 19 | 2.75 | 8.083 | 2.839 | 7.09 | 55 | 1.98 | 70.7 | 0.338 | 0.025 | 35.23 | 8488 | 8.23 | 58 |  | 167.53 | 2.98 | 6.8 | -3.852 | 0.23 | 101
8/16/2025 05:30 | 8 | 19 | 2.75 | 8.064 | 2.893 | 7.09 | 55 | 1.98 | 70.7 | 0.338 | 0.025 | 35.23 | 8488 | 8.24 | 58 |  | 170.18 | 3.04 | 6.8 | -3.852 | 0.28 | 101
8/16/2025 05:45 | 8 | 19 | 2.75 | 8.115 | 3.005 | 7.08 | 55 | 1.98 | 70.7 | 0.338 | 0.025 | 35.23 | 8488 | 8.23 | 58 |  | 167.6 | 2.97 | 6.8 | -3.852 | 0.23 | 101
8/16/2025 06:00 | 10 | 19 | 2.75 | 8.03 | 3.077 | 7.08 | 55 | 1.98 | 70.5 | 0.338 | 0.025 | 35.23 | 8488 | 8.2 | 58 |  | 169.05 | 3.03 | 6.8 | -3.852 | 0.21 | 101
8/16/2025 06:15 | 12 | 19 | 2.75 | 8.032 | 2.987 | 7.08 | 55 | 1.98 | 70.5 | 0.338 | 0.025 | 35.23 | 8488 | 8.16 | 58 |  | 168.14 | 3.01 | 6.8 | -3.852 | 0.22 | 101
8/16/2025 06:30 | 9 | 19 | 2.75 | 8.084 | 3.215 | 7.08 | 55 | 1.98 | 70.5 | 0.338 | 0.025 | 35.23 | 8488 | 8.12 | 58 |  | 166.36 | 2.96 | 6.79 | -3.852 | 0.23 | 101
8/16/2025 06:45 | 6 | 19 | 2.75 | 8.066 | 3.17 | 7.08 | 55 | 1.98 | 70.5 | 0.338 | 0.025 | 35.23 | 8488 | 8.11 | 58 |  | 167.26 | 2.99 | 6.8 | -3.852 | 0.26 | 101
8/16/2025 07:00 | 9 | 19 | 2.75 | 8.073 | 3.247 | 7.08 | 55 | 1.98 | 70.5 | 0.338 | 0.024 | 35.23 | 8488 | 8.12 | 58 |  | 168.53 | 3.01 | 6.8 | -3.852 | 0.23 | 101
8/16/2025 07:15 | 8 | 19 | 2.75 | 8.004 | 3.246 | 7.08 | 55 | 1.98 | 70.5 | 0.338 | 0.024 | 35.23 | 8488 | 8.12 | 58 |  | 167.29 | 3.01 | 6.8 | -3.852 | 0.24 | 101
8/16/2025 07:30 | 10 | 19 | 2.75 | 8.116 | 3.342 | 7.08 | 55 | 1.98 | 70.5 | 0.338 | 0.024 | 35.23 | 8488 | 8.13 | 58 |  | 170.16 | 3.02 | 6.8 | -3.852 | 0.22 | 101
8/16/2025 07:45 | 10 | 19 | 2.75 | 8.131 | 3.194 | 7.09 | 55 | 1.98 | 70.5 | 0.338 | 0.024 | 35.23 | 8488 | 8.13 | 58 |  | 169.93 | 3.01 | 6.81 | -3.852 | 0.21 | 101
8/16/2025 08:00 | 8 | 19 | 2.75 | 8.091 | 3.159 | 7.09 | 55 | 1.98 | 70.5 | 0.325 | 0.024 | 35.23 | 8488 | 8.12 | 58 |  | 168.82 | 3 | 6.82 | -3.852 | 0.23 | 101
8/16/2025 08:15 | 10 | 19 | 2.75 | 8.02 | 3.14 | 7.09 | 55 | 1.98 | 70.5 | 0.325 | 0.024 | 35.23 | 8488 | 8.12 | 58 |  | 168.29 | 3.02 | 6.82 | -3.852 | 0.23 | 101
8/16/2025 08:30 | 8 | 19 | 2.75 | 8.285 | 3.046 | 7.1 | 55 | 1.98 | 70.5 | 0.325 | 0.024 | 35.23 | 8488 | 8.12 | 58 |  | 172.41 | 3 | 6.83 | -3.852 | 0.22 | 101
8/16/2025 08:45 | 6 | 19 | 2.75 | 8.257 | 3.044 | 7.1 | 55 | 1.98 | 70.5 | 0.325 | 0.024 | 35.23 | 8488 | 8.12 | 58 |  | 172.79 | 3.01 | 6.83 | -3.852 | 0.23 | 101
8/16/2025 09:00 | 7 | 19 | 2.75 | 8.261 | 10.569 | 7.1 | 55 | 1.98 | 70.5 | 0.325 | 0.024 | 35.23 | 8488 | 8.12 | 58 |  | 172.61 | 3.01 | 6.82 | -3.852 | 0.22 | 101
8/16/2025 09:15 | 7 | 19 | 2.75 | 7.864 | 6.256 | 7.09 | 55 | 1.98 | 70.5 | 0.325 | 0.024 | 35.23 | 8488 | 8.11 | 58 |  | 165.25 | 3.03 | 6.82 | -3.852 | 0.24 | 101
8/16/2025 09:30 | 5 | 19 | 2.75 | 7.632 | 5.305 | 7.09 | 55 | 1.98 | 70.5 | 0.325 | 0.024 | 35.23 | 8488 | 8.11 | 58 |  | 160.11 | 3.02 | 6.82 | -3.852 | 0.21 | 101
8/16/2025 09:45 | 5 | 19 | 2.75 | 7.923 | 4.6 | 7.09 | 55 | 1.98 | 70.5 | 0.325 | 0.024 | 35.23 | 8488 | 8.11 | 58 |  | 164.4 | 2.99 | 6.81 | -3.852 | 0.22 | 101
8/16/2025 10:00 | 8 | 19 | 2.75 | 7.97 | 4.382 | 7.09 | 54 | 1.98 | 70.3 | 0.325 | 0.024 | 35.23 | 8488 | 8.11 | 58 |  | 166.45 | 3.01 | 6.81 | -3.852 | 0.23 | 101
8/16/2025 10:15 | 6 | 19 | 2.75 | 7.955 | 3.941 | 7.09 | 54 | 1.98 | 70.3 | 0.325 | 0.024 | 35.23 | 8488 | 8.11 | 58 |  | 164.41 | 2.98 | 6.82 | -3.852 | 0.21 | 101
8/16/2025 10:30 | 5 | 19 | 2.75 | 7.862 | 4.091 | 7.09 | 54 | 1.98 | 70.3 | 0.325 | 0.024 | 35.23 | 8488 | 8.11 | 58 |  | 164.27 | 3.01 | 6.82 | -3.852 | 0.23 | 101
8/16/2025 10:45 | 5 | 19 | 2.75 | 7.939 | 3.39 | 7.1 | 54 | 1.98 | 70.3 | 0.325 | 0.024 | 35.23 | 8488 | 8.11 | 58 |  | 164.35 | 2.98 | 6.82 | -3.852 | 0.25 | 101
8/16/2025 11:00 | 4 | 19 | 2.75 | 7.893 | 2.994 | 7.1 | 54 | 1.98 | 70.3 | 0.325 | 0.024 | 35.23 | 8488 | 8.11 | 58 |  | 164.89 | 3.01 | 6.82 | -3.852 | 0.24 | 101
8/16/2025 11:15 | 8 | 19 | 2.75 | 7.874 | 2.866 | 7.1 | 54 | 1.98 | 70.3 | 0.325 | 0.023 | 35.23 | 8488 | 8.12 | 58 |  | 164.58 | 3.01 | 6.82 | -3.852 | 0.23 | 101
8/16/2025 11:30 | 10 | 19 | 2.75 | 7.922 | 3.112 | 7.12 | 54 | 1.98 | 70.3 | 0.325 | 0.023 | 35.23 | 8488 | 8.12 | 58 |  | 82.33 | 1.5 | 6.83 | -3.852 | 0.23 | 101
8/16/2025 11:45 | 9 | 19 | 2.75 | 7.922 | 2.969 | 7.13 | 54 | 1.98 | 70.3 | 0.325 | 0.023 | 35.23 | 8488 | 8.12 | 58 |  | 82.6 | 1.5 | 6.84 | -3.852 | 0.23 | 101
8/16/2025 12:00 | 2 | 19 | 2.75 | 7.801 | 2.857 | 7.14 | 54 | 1.98 | 70.3 | 0.205 | 0.023 | 35.23 | 8488 | 8.13 | 58 |  | 81.8 | 1.51 | 6.84 | -3.852 | 0.23 | 101
8/16/2025 12:15 | 5 | 19 | 2.75 | 7.398 | 2.755 | 7.14 | 54 | 1.98 | 70.3 | 0.205 | 0.023 | 35.23 | 8488 | 8.13 | 58 |  | 77.04 | 1.5 | 6.91 | -3.852 | 0.5 | 101
8/16/2025 12:30 | 0 | 19 | 2.75 | 7.846 | 4.481 | 7.11 | 54 | 1.98 | 70.3 | 0.205 | 0.023 | 35.23 | 8488 | 8.14 | 58 |  | 81.62 | 1.5 | 6.78 | -3.852 | 0.23 | 101
8/16/2025 12:45 | 2 | 19 | 2.75 | 7.835 | 2.528 | 7.12 | 54 | 1.98 | 70.3 | 0.205 | 0.023 | 35.23 | 8488 | 8.14 | 58 |  | 82.08 | 1.51 | 6.79 | -3.852 | 0.23 | 101
8/16/2025 13:00 | 4 | 19 | 2.75 | 7.914 | 2.63 | 7.15 | 54 | 1.98 | 70.3 | 0.205 | 0.023 | 35.23 | 8488 | 8.14 | 58 |  | 82.04 | 1.49 | 6.87 | -3.852 | 0.23 | 101
8/16/2025 13:15 | 6 | 19 | 2.75 | 7.901 | 2.603 | 7.16 | 54 | 1.98 | 70.3 | 0.205 | 0.023 | 35.23 | 8488 | 8.13 | 58 |  | 82.39 | 1.5 | 6.88 | -3.852 | 0.24 | 101
8/16/2025 13:30 | 6 | 19 | 2.75 | 7.895 | 2.541 | 7.16 | 54 | 1.98 | 70.3 | 0.205 | 0.023 | 35.23 | 8488 | 8.14 | 58 |  | 82.24 | 1.5 | 6.87 | -3.852 | 0.24 | 101
8/16/2025 13:45 | 5 | 19 | 2.75 | 7.831 | 2.423 | 7.17 | 54 | 1.98 | 70.3 | 0.205 | 0.023 | 35.23 | 8488 | 8.14 | 58 |  | 81.97 | 1.51 | 6.87 | -3.852 | 0.24 | 101
8/16/2025 14:00 | 5 | 19 | 2.75 | 7.314 | 2.432 | 7.17 | 54 | 1.98 | 70.5 | 0.205 | 0.023 | 35.23 | 8488 | 8.14 | 56 |  | 75.78 | 1.49 | 6.86 | -3.852 | 0.24 | 101
8/16/2025 14:15 | 6 | 19 | 2.75 | 7.37 | 2.406 | 7.16 | 54 | 1.98 | 70.5 | 0.205 | 0.023 | 35.23 | 8488 | 8.13 | 56 |  | 76.65 | 1.5 | 6.86 | -3.852 | 0.23 | 101
8/16/2025 14:30 | 4 | 19 | 2.75 | 7.716 | 2.406 | 7.16 | 54 | 1.98 | 70.5 | 0.205 | 0.023 | 34.68 | 8528 | 8.13 | 56 |  | 80.52 | 1.5 | 6.85 | -3.852 | 0.23 | 101
8/16/2025 14:45 | 8 | 19 | 2.75 | 7.728 | 2.602 | 7.15 | 54 | 1.98 | 70.5 | 0.205 | 0.024 | 34.68 | 8528 | 8.13 | 56 |  | 80.03 | 1.49 | 6.84 | -3.852 | 0.23 | 101
8/16/2025 15:00 | 9 | 19 | 2.75 | 7.869 | 2.735 | 7.15 | 54 | 1.98 | 70.5 | 0.205 | 0.025 | 34.68 | 8528 | 8.12 | 56 |  | 81.8 | 1.5 | 6.83 | -3.852 | 0.22 | 101
8/16/2025 15:15 | 9 | 19 | 2.75 | 7.879 | 2.994 | 7.13 | 54 | 1.98 | 70.5 | 0.205 | 0.025 | 34.68 | 8528 | 8.12 | 56 |  | 82.12 | 1.5 | 6.82 | -3.852 | 0.2 | 101
8/16/2025 15:30 | 8 | 19 | 2.75 | 7.851 | 3.161 | 7.12 | 54 | 1.98 | 70.5 | 0.205 | 0.025 | 34.68 | 8528 | 8.11 | 56 |  | 81.9 | 1.5 | 6.81 | -3.852 | 0.22 | 101
8/16/2025 15:45 | 8 | 19 | 2.75 | 7.847 | 3.275 | 7.13 | 54 | 1.98 | 70.5 | 0.205 | 0.025 | 34.68 | 8528 | 8.1 | 56 |  | 81.74 | 1.5 | 6.81 | -3.852 | 0.22 | 101
8/16/2025 16:00 | 9 | 19 | 2.75 | 7.357 | 3.206 | 7.14 | 54 | 1.98 | 70.5 | 0.173 | 0.025 | 34.68 | 8528 | 8.13 | 56 |  | 76.88 | 1.5 | 6.82 | -3.852 | 0.21 | 101
8/16/2025 16:15 | 7 | 19 | 2.75 | 7.587 | 3.089 | 7.15 | 54 | 1.98 | 70.5 | 0.173 | 0.025 | 34.03 | 8645 | 8.18 | 56 |  | 79.21 | 1.5 | 6.83 | -3.852 | 0.22 | 101
8/16/2025 16:30 | 8 | 19 | 2.75 | 7.764 | 2.967 | 7.16 | 54 | 1.98 | 70.5 | 0.173 | 0.026 | 34.03 | 8645 | 8.22 | 56 |  | 81.6 | 1.51 | 6.83 | -3.852 | 0.24 | 101
8/16/2025 16:45 | 8 | 19 | 2.75 | 7.787 | 2.846 | 7.16 | 54 | 1.98 | 70.5 | 0.173 | 0.026 | 34.03 | 8645 | 8.23 | 56 |  | 81.43 | 1.51 | 6.84 | -3.852 | 0.22 | 101
8/16/2025 17:00 | 9 | 19 | 2.75 | 7.842 | 2.861 | 7.16 | 54 | 1.98 | 70.5 | 0.173 | 0.026 | 34.03 | 8645 | 8.23 | 56 |  | 81.64 | 1.5 | 6.84 | -3.852 | 0.23 | 101
8/16/2025 17:15 | 7 | 19 | 2.75 | 7.807 | 2.998 | 7.15 | 54 | 1.98 | 70.5 | 0.173 | 0.026 | 34.03 | 8645 | 8.21 | 56 |  | 80.71 | 1.49 | 6.82 | -3.852 | 0.24 | 101
8/16/2025 17:30 | 9 | 19 | 2.75 | 7.261 | 3.668 | 7.13 | 54 | 1.98 | 70.5 | 0.173 | 0.025 | 34.03 | 8645 | 8.19 | 56 |  | 75.74 | 1.5 | 6.8 | -3.852 | 0.2 | 101
8/16/2025 17:45 | 4 | 19 | 2.75 | 7.316 | 3.743 | 7.11 | 54 | 1.98 | 70.5 | 0.173 | 0.025 | 34.03 | 8645 | 8.2 | 56 |  | 75.65 | 1.49 | 6.79 | -3.852 | 0.2 | 101
8/16/2025 18:00 | 5 | 19 | 2.75 | 7.625 | 3.459 | 7.14 | 54 | 1.98 | 70.7 | 0.173 | 0.025 | 34.03 | 8645 | 8.23 | 56 |  | 79.12 | 1.49 | 6.81 | -3.852 | 0.21 | 101
8/16/2025 18:15 | 8 | 19 | 2.75 | 7.608 | 3.147 | 7.16 | 54 | 1.98 | 70.7 | 0.173 | 0.025 | 34.03 | 8645 | 8.25 | 56 |  | 79.32 | 1.5 | 6.83 | -3.852 | 0.22 | 101
8/16/2025 18:30 | 10 | 19 | 2.75 | 7.573 | 2.435 | 7.16 | 54 | 1.98 | 70.7 | 0.173 | 0.025 | 34.03 | 8645 | 8.26 | 56 |  | 78.92 | 1.5 | 6.84 | -3.852 | 0.25 | 101
8/16/2025 18:45 | 7 | 19 | 2.75 | 7.546 | 2.665 | 7.17 | 54 | 1.98 | 70.7 | 0.173 | 0.025 | 34.03 | 8645 | 8.26 | 56 |  | 78.77 | 1.5 | 6.85 | -3.852 | 0.23 | 101
8/16/2025 19:00 | 9 | 19 | 2.75 | 7.56 | 2.691 | 7.16 | 54 | 1.98 | 70.7 | 0.173 | 0.025 | 34.03 | 8645 | 8.26 | 56 |  | 78.61 | 1.5 | 6.83 | -3.852 | 0.22 | 101
8/16/2025 19:15 | 8 | 19 | 2.75 | 7.543 | 2.782 | 7.15 | 54 | 1.98 | 70.7 | 0.173 | 0.025 | 34.03 | 8645 | 8.25 | 56 |  | 78.92 | 1.51 | 6.82 | -3.852 | 0.23 | 101
8/16/2025 19:30 | 8 | 19 | 2.75 | 7.519 | 2.832 | 7.14 | 54 | 1.98 | 70.7 | 0.173 | 0.025 | 34.03 | 8645 | 8.25 | 56 |  | 78.93 | 1.51 | 6.81 | -3.852 | 0.24 | 101
8/16/2025 19:45 | 9 | 19 | 2.75 | 7.629 | 2.76 | 7.14 | 54 | 1.98 | 70.7 | 0.173 | 0.025 | 34.03 | 8645 | 8.24 | 56 |  | 79.7 | 1.5 | 6.81 | -3.852 | 0.25 | 101
8/16/2025 20:00 | 8 | 19 | 2.75 | 7.655 | 2.907 | 7.14 | 54 | 1.98 | 70.7 | 0.192 | 0.025 | 34.03 | 8645 | 8.23 | 56 |  | 79.93 | 1.5 | 6.81 | -3.852 | 0.22 | 101
8/16/2025 20:15 | 7 | 19 | 2.75 | 7.25 | 3.061 | 7.12 | 54 | 1.98 | 70.7 | 0.192 | 0.025 | 34.03 | 8645 | 8.23 | 56 |  | 113.47 | 2.25 | 6.8 | -3.852 | 0.21 | 101
8/16/2025 20:30 | 9 | 19 | 2.75 | 7.221 | 2.88 | 7.1 | 54 | 1.98 | 70.7 | 0.192 | 0.025 | 34.03 | 8645 | 8.22 | 56 |  | 150.5 | 3 | 6.79 | -3.852 | 0.22 | 101
8/16/2025 20:45 | 9 | 19 | 2.75 | 7.637 | 2.914 | 7.1 | 54 | 1.98 | 70.7 | 0.192 | 0.025 | 34.03 | 8645 | 8.23 | 56 |  | 159.14 | 3 | 6.8 | -3.852 | 0.23 | 101
8/16/2025 21:00 | 7 | 19 | 2.75 | 7.91 | 2.845 | 7.11 | 54 | 1.98 | 70.7 | 0.192 | 0.025 | 34.03 | 8645 | 8.22 | 56 |  | 164.23 | 2.99 | 6.8 | -3.852 | 0.23 | 101
8/16/2025 21:15 | 9 | 19 | 2.75 | 7.928 | 2.722 | 7.12 | 54 | 1.98 | 70.7 | 0.192 | 0.025 | 34.03 | 8645 | 8.21 | 56 |  | 165 | 3 | 6.81 | -3.852 | 0.23 | 101
8/16/2025 21:30 | 9 | 19 | 2.75 | 7.931 | 2.713 | 7.12 | 54 | 1.98 | 70.7 | 0.192 | 0.025 | 34.03 | 8645 | 8.21 | 56 |  | 165.24 | 3 | 6.82 | -3.852 | 0.24 | 101
8/16/2025 21:45 | 9 | 19 | 2.75 | 7.81 | 2.75 | 7.12 | 54 | 1.98 | 70.7 | 0.192 | 0.025 | 34.03 | 8645 | 8.21 | 56 |  | 164.38 | 3.03 | 6.82 | -3.852 | 0.23 | 101
8/16/2025 22:00 | 7 | 19 | 2.75 | 7.519 | 2.725 | 7.12 | 56 | 1.98 | 70.5 | 0.192 | 0.025 | 34.03 | 8645 | 8.2 | 56 |  | 156.04 | 2.99 | 6.82 | -3.852 | 0.22 | 101
8/16/2025 22:15 | 8 | 19 | 2.75 | 7.424 | 2.653 | 7.12 | 56 | 1.98 | 70.5 | 0.192 | 0.025 | 34.03 | 8645 | 8.2 | 56 |  | 153.91 | 2.99 | 6.82 | -3.852 | 0.23 | 101
8/16/2025 22:30 | 9 | 19 | 2.75 | 7.754 | 2.703 | 7.12 | 56 | 1.98 | 70.5 | 0.192 | 0.025 | 34.03 | 8645 | 8.2 | 56 |  | 162.98 | 3.03 | 6.81 | -3.852 | 0.28 | 101
8/16/2025 22:45 | 6 | 19 | 2.75 | 7.825 | 2.684 | 7.12 | 56 | 1.98 | 70.5 | 0.192 | 0.025 | 34.03 | 8645 | 8.2 | 56 |  | 162.34 | 2.99 | 6.81 | -3.852 | 0.23 | 101
8/16/2025 23:00 | 4 | 19 | 2.75 | 7.778 | 2.682 | 7.13 | 56 | 1.98 | 70.5 | 0.192 | 0.025 | 34.03 | 8645 | 8.2 | 56 |  | 162.68 | 3.01 | 6.81 | -3.852 | 0.22 | 101
8/16/2025 23:15 | 6 | 19 | 2.75 | 7.333 | 2.815 | 7.12 | 56 | 1.98 | 70.5 | 0.192 | 0.025 | 34.03 | 8645 | 8.2 | 56 |  | 151.99 | 2.98 | 6.8 | -3.852 | 0.21 | 101
8/16/2025 23:30 | 7 | 19 | 2.75 | 7.225 | 39.937 | 7.11 | 56 | 1.98 | 70.5 | 0.192 | 0.025 | 34.03 | 8645 | 8.2 | 56 |  | 149.79 | 2.99 | 6.8 | -3.852 | 0.24 | 101
8/16/2025 23:45 | 3 | 19 | 2.75 | 7.955 | 5.487 | 7.11 | 56 | 1.98 | 70.5 | 0.192 | 0.025 | 34.03 | 8645 | 8.2 | 56 |  | 164.79 | 2.98 | 6.81 | -3.852 | 0.21 | 101
8/17/2025 00:00 | 4 | 19 | 2.75 | 7.925 | 3.734 | 7.11 | 56 | 1.98 | 70.5 | 0.211 | 0.025 | 34.03 | 8645 | 8.19 | 56 |  | 164.27 | 2.98 | 6.82 | -3.852 | 0.22 | 101
8/17/2025 00:15 | 7 | 19 | 2.75 | 7.193 | 3.529 | 7.11 | 56 | 1.98 | 70.5 | 0.211 | 0.025 | 34.03 | 8645 | 8.18 | 56 |  | 149.63 | 3 | 6.84 | -3.852 | 0.22 | 101
8/17/2025 00:30 | 8 | 19 | 2.75 | 7.163 | 2.731 | 7.11 | 56 | 1.98 | 70.5 | 0.211 | 0.025 | 34.03 | 8645 | 8.18 | 56 |  | 149.39 | 3 | 6.85 | -3.852 | 0.23 | 101
8/17/2025 00:45 | 8 | 19 | 2.75 | 7.125 | 2.211 | 7.12 | 56 | 1.98 | 70.5 | 0.211 | 0.025 | 34.03 | 8645 | 8.17 | 56 |  | 150.06 | 3.03 | 6.86 | -3.852 | 0.22 | 101
8/17/2025 01:00 | 6 | 19 | 2.75 | 7.468 | 2.756 | 7.1 | 56 | 1.98 | 70.5 | 0.211 | 0.025 | 34.03 | 8645 | 8.17 | 56 |  | 156.06 | 3.01 | 6.82 | -3.852 | 0.22 | 101
8/17/2025 01:15 | 3 | 19 | 2.75 | 7.468 | 2.921 | 7.08 | 56 | 1.98 | 70.5 | 0.211 | 0.025 | 34.03 | 8645 | 8.17 | 56 |  | 156.2 | 3.01 | 6.78 | -3.852 | 0.23 | 101
8/17/2025 01:30 | 5 | 19 | 2.75 | 7.36 | 3.141 | 7.08 | 56 | 1.98 | 70.5 | 0.211 | 0.025 | 34.03 | 8645 | 8.17 | 56 |  | 155.62 | 3.04 | 6.76 | -3.852 | 0.21 | 101
8/17/2025 01:45 | 8 | 19 | 2.75 | 7.492 | 3.066 | 7.08 | 56 | 1.98 | 70.5 | 0.211 | 0.025 | 34.03 | 8645 | 8.17 | 56 |  | 155.18 | 2.98 | 6.77 | -3.852 | 0.21 | 101
8/17/2025 02:00 | 4 | 19 | 2.75 | 7.463 | 3.199 | 7.07 | 56 | 1.98 | 70.5 | 0.211 | 0.024 | 34.03 | 8645 | 8.17 | 58 |  | 154.76 | 2.99 | 6.77 | -3.852 | 0.22 | 101
8/17/2025 02:15 | 9 | 19 | 2.75 | 7.171 | 3.182 | 7.07 | 56 | 1.98 | 70.5 | 0.211 | 0.024 | 34.03 | 8645 | 8.17 | 58 |  | 149.36 | 3 | 6.77 | -3.852 | 0.21 | 101
8/17/2025 02:30 | 9 | 19 | 2.75 | 7.383 | 2.884 | 7.08 | 56 | 1.98 | 70.5 | 0.211 | 0.025 | 33.24 | 8569 | 8.16 | 58 |  | 177.03 | 3.45 | 6.79 | -3.852 | 0.22 | 101
8/17/2025 02:45 | 9 | 19 | 2.75 | 7.704 | 2.735 | 7.09 | 56 | 1.98 | 70.5 | 0.211 | 0.025 | 33.24 | 8569 | 8.16 | 58 |  | 176.46 | 3.3 | 6.8 | -3.852 | 0.23 | 101
8/17/2025 03:00 | 2 | 19 | 2.75 | 7.589 | 2.749 | 7.09 | 56 | 1.98 | 70.5 | 0.211 | 0.026 | 33.24 | 8569 | 8.16 | 58 |  | 176.7 | 3.35 | 6.8 | -3.852 | 0.21 | 101
8/17/2025 03:15 | 10 | 19 | 2.75 | 7.496 | 2.841 | 7.09 | 56 | 1.98 | 70.5 | 0.211 | 0.026 | 33.24 | 8569 | 8.16 | 58 |  | 176.91 | 3.4 | 6.8 | -3.852 | 0.21 | 101
8/17/2025 03:30 | 5 | 19 | 2.75 | 7.514 | 2.823 | 7.09 | 56 | 1.98 | 70.5 | 0.211 | 0.026 | 33.24 | 8569 | 8.16 | 58 |  | 176.89 | 3.39 | 6.81 | -3.852 | 0.24 | 101
8/17/2025 03:45 | 9 | 19 | 2.75 | 7.463 | 2.79 | 7.09 | 56 | 1.98 | 70.5 | 0.211 | 0.026 | 33.24 | 8569 | 8.15 | 58 |  | 176.9 | 3.41 | 6.81 | -3.852 | 0.23 | 101
8/17/2025 04:00 | 6 | 19 | 2.75 | 7.519 | 2.592 | 7.11 | 56 | 1.98 | 70.5 | 0.266 | 0.026 | 33.24 | 8569 | 8.14 | 58 |  | 177.28 | 3.4 | 6.82 | -3.852 | 0.25 | 101
8/17/2025 04:15 | 7 | 19 | 2.75 | 7.537 | 2.508 | 7.12 | 56 | 1.98 | 70.5 | 0.266 | 0.026 | 33.24 | 8569 | 8.17 | 58 |  | 176.37 | 3.37 | 6.83 | -3.852 | 0.22 | 101
8/17/2025 04:30 | -5 | 19 | 2.75 | 7.61 | 2.347 | 7.12 | 56 | 1.98 | 70.5 | 0.266 | 0.026 | 33.24 | 8569 | 8.19 | 58 |  | 176.6 | 3.34 | 6.84 | -3.852 | 0.21 | 101
8/17/2025 04:45 | -14 | 19 | 2.75 | 7.534 | 2.572 | 7.1 | 56 | 1.98 | 70.5 | 0.266 | 0.026 | 33.24 | 8569 | 8.21 | 58 |  | 176.68 | 3.38 | 6.82 | -3.852 | 0.2 | 100
8/17/2025 05:00 | 3 | 19 | 2.75 | 6.958 | 2.789 | 7.08 | 56 | 1.98 | 70.5 | 0.266 | 0.025 | 33.24 | 8569 | 8.2 | 58 |  | 169.4 | 3.51 | 6.8 | -3.852 | 0.2 | 101
8/17/2025 05:15 | 0 | 19 | 2.75 | 6.834 | 2.862 | 7.08 | 56 | 1.98 | 70.5 | 0.266 | 0.025 | 33.24 | 8569 | 8.2 | 58 |  | 165.61 | 3.49 | 6.79 | -3.852 | 0.27 | 101
8/17/2025 05:30 | 4 | 19 | 2.75 | 7.195 | 2.889 | 7.08 | 56 | 1.98 | 70.5 | 0.266 | 0.025 | 33.24 | 8569 | 8.19 | 58 |  | 175.62 | 3.51 | 6.79 | -3.852 | 0.22 | 101
8/17/2025 05:45 | 4 | 19 | 2.75 | 7.236 | 2.888 | 7.07 | 56 | 1.98 | 70.5 | 0.266 | 0.025 | 33.24 | 8569 | 8.18 | 58 |  | 175.86 | 3.5 | 6.79 | -3.852 | 0.24 | 101
8/17/2025 06:00 | 2 | 19 | 2.75 | 7.25 | 3.035 | 7.07 | 56 | 1.98 | 70.3 | 0.266 | 0.025 | 33.24 | 8569 | 8.16 | 58 |  | 175.11 | 3.48 | 6.79 | -3.852 | 0.19 | 101
8/17/2025 06:15 | 2 | 19 | 2.75 | 7.246 | 3.013 | 7.07 | 56 | 1.98 | 70.3 | 0.266 | 0.025 | 33.24 | 8569 | 8.15 | 58 |  | 175.61 | 3.49 | 6.79 | -3.852 | 0.21 | 101
8/17/2025 06:30 | 3 | 19 | 2.75 | 7.218 | 3.076 | 7.06 | 56 | 1.98 | 70.3 | 0.266 | 0.025 | 33.24 | 8569 | 8.14 | 58 |  | 175.9 | 3.51 | 6.79 | -3.852 | 0.23 | 101
8/17/2025 06:45 | 4 | 19 | 2.75 | 7.203 | 3.025 | 7.07 | 56 | 1.98 | 70.3 | 0.266 | 0.025 | 33.24 | 8569 | 8.13 | 58 |  | 175.44 | 3.51 | 6.79 | -3.852 | 0.2 | 101
8/17/2025 07:00 | 2 | 19 | 2.75 | 7.142 | 3.096 | 7.08 | 56 | 1.98 | 70.3 | 0.266 | 0.025 | 33.24 | 8569 | 8.13 | 58 |  | 174.05 | 3.51 | 6.8 | -3.852 | 0.22 | 101
8/17/2025 07:15 | 3 | 19 | 2.75 | 6.694 | 3.288 | 7.08 | 56 | 1.98 | 70.3 | 0.266 | 0.025 | 33.24 | 8569 | 8.12 | 58 |  | 163.24 | 3.51 | 6.8 | -3.852 | 0.23 | 101
8/17/2025 07:30 | 4 | 19 | 2.75 | 7.257 | 3.24 | 7.08 | 56 | 1.98 | 70.3 | 0.266 | 0.025 | 33.24 | 8569 | 8.12 | 58 |  | 176.1 | 3.49 | 6.81 | -3.852 | 0.2 | 101
8/17/2025 07:45 | 0 | 19 | 2.75 | 7.259 | 3.394 | 7.08 | 56 | 1.98 | 70.3 | 0.266 | 0.024 | 33.24 | 8569 | 8.12 | 58 |  | 176 | 3.49 | 6.81 | -3.852 | 0.21 | 101
8/17/2025 08:00 | 3 | 19 | 2.75 | 7.228 | 3.538 | 7.07 | 56 | 1.98 | 70.3 | 0.306 | 0.024 | 33.24 | 8569 | 8.11 | 58 |  | 175.77 | 3.5 | 6.81 | -3.852 | 0.2 | 101
8/17/2025 08:15 | -2 | 19 | 2.75 | 7.22 | 3.461 | 7.08 | 56 | 1.98 | 70.3 | 0.306 | 0.024 | 33.24 | 8569 | 8.11 | 58 |  | 175.91 | 3.51 | 6.82 | -3.852 | 0.2 | 101
8/17/2025 08:30 | -1 | 19 | 2.75 | 7.244 | 3.576 | 7.08 | 56 | 1.98 | 70.3 | 0.306 | 0.024 | 33.24 | 8569 | 8.11 | 58 |  | 175.98 | 3.5 | 6.82 | -3.852 | 0.2 | 101
8/17/2025 08:45 | 0 | 19 | 2.75 | 7.478 | 3.617 | 7.08 | 56 | 1.98 | 70.3 | 0.306 | 0.024 | 33.24 | 8569 | 8.11 | 58 |  | 175.97 | 3.39 | 6.82 | -3.852 | 0.19 | 101
8/17/2025 09:00 | 3 | 19 | 2.75 | 7.458 | 3.562 | 7.08 | 56 | 1.98 | 70.3 | 0.306 | 0.024 | 33.24 | 8569 | 8.11 | 58 |  | 175.86 | 3.4 | 6.82 | -3.852 | 0.2 | 101
8/17/2025 09:15 | 4 | 19 | 2.75 | 7.524 | 3.375 | 7.09 | 56 | 1.98 | 70.3 | 0.306 | 0.024 | 33.24 | 8569 | 8.11 | 58 |  | 179.83 | 3.44 | 6.82 | -3.852 | 0.21 | 101
8/17/2025 09:30 | 3 | 19 | 2.75 | 7.514 | 3.574 | 7.09 | 56 | 1.98 | 70.3 | 0.306 | 0.024 | 33.24 | 8569 | 8.12 | 58 |  | 179.75 | 3.44 | 6.82 | -3.852 | 0.2 | 101
8/17/2025 09:45 | -1 | 19 | 2.75 | 7.548 | 3.12 | 7.09 | 56 | 1.98 | 70.3 | 0.306 | 0.024 | 33.24 | 8569 | 8.12 | 58 |  | 179.96 | 3.43 | 6.82 | -3.852 | 0.19 | 101
8/17/2025 10:00 | -13 | 19 | 2.75 | 7.556 | 2.918 | 7.1 | 54 | 1.98 | 70.3 | 0.306 | 0.024 | 33.24 | 8569 | 8.14 | 58 |  | 179.79 | 3.43 | 6.82 | -3.852 | 0.2 | 100
8/17/2025 10:15 | -4 | 19 | 2.75 | 7.5 | 2.88 | 7.1 | 54 | 1.98 | 70.3 | 0.306 | 0.024 | 33.24 | 8569 | 8.16 | 58 |  | 179.88 | 3.45 | 6.82 | -3.852 | 0.2 | 101
8/17/2025 10:30 | 3 | 19 | 2.75 | 7.54 | 2.801 | 7.1 | 54 | 1.98 | 70.3 | 0.306 | 0.024 | 33.24 | 8569 | 8.18 | 58 |  | 180.21 | 3.44 | 6.82 | -3.852 | 0.19 | 101
8/17/2025 10:45 | 3 | 19 | 2.75 | 8.053 | 2.569 | 7.1 | 54 | 1.98 | 70.3 | 0.306 | 0.024 | 33.24 | 8569 | 8.19 | 58 |  | 179.43 | 3.21 | 6.82 | -3.852 | 0.21 | 101
8/17/2025 11:00 | 5 | 19 | 2.75 | 8.028 | 2.551 | 7.1 | 54 | 1.98 | 70.3 | 0.306 | 0.024 | 33 | 8527 | 8.2 | 58 |  | 180.09 | 3.23 | 6.82 | -3.852 | 0.2 | 101
8/17/2025 11:15 | 5 | 19 | 2.75 | 8.071 | 2.463 | 7.1 | 54 | 1.98 | 70.3 | 0.306 | 0.025 | 33 | 8527 | 8.21 | 58 |  | 180.18 | 3.21 | 6.82 | -3.852 | 0.2 | 101
8/17/2025 11:30 | 3 | 19 | 2.75 | 8.037 | 2.474 | 7.1 | 54 | 1.98 | 70.3 | 0.306 | 0.026 | 33 | 8527 | 8.22 | 58 |  | 180.04 | 3.23 | 6.82 | -3.852 | 0.19 | 101
8/17/2025 11:45 | -6 | 19 | 2.75 | 8.066 | 1.893 | 7.06 | 54 | 1.98 | 70.3 | 0.306 | 0.026 | 33 | 8527 | 8.21 | 58 |  | 179.71 | 3.21 | 6.75 | -3.852 | 0.23 | 101
8/17/2025 12:00 | 0 | 19 | 2.75 | 7.955 | 1.921 | 7.1 | 54 | 1.98 | 70.3 | 0.171 | 0.025 | 33 | 8527 | 8.19 | 58 |  | 180.13 | 3.26 | 6.75 | -3.852 | 0.24 | 101
8/17/2025 12:15 | 5 | 19 | 2.75 | 7.979 | 1.771 | 7.12 | 54 | 1.98 | 70.3 | 0.171 | 0.025 | 33 | 8527 | 8.17 | 58 |  | 180.42 | 3.26 | 6.8 | -3.852 | 0.26 | 101
8/17/2025 12:30 | 0 | 19 | 2.75 | 8.026 | 1.664 | 7.13 | 54 | 1.98 | 70.3 | 0.171 | 0.025 | 33 | 8527 | 8.19 | 58 |  | 180.48 | 3.24 | 6.84 | -3.852 | 0.21 | 101
8/17/2025 12:45 | 7 | 19 | 2.75 | 7.992 | 1.609 | 7.13 | 54 | 1.98 | 70.3 | 0.171 | 0.025 | 33 | 8527 | 8.22 | 58 |  | 180.1 | 3.25 | 6.86 | -3.852 | 0.23 | 101
8/17/2025 13:00 | 7 | 19 | 2.75 | 7.95 | 1.563 | 7.14 | 54 | 1.98 | 70.3 | 0.171 | 0.025 | 33 | 8527 | 8.24 | 58 |  | 180.24 | 3.26 | 6.86 | -3.852 | 0.25 | 101
8/17/2025 13:15 | 5 | 19 | 2.75 | 7.239 | 1.544 | 7.14 | 54 | 1.98 | 70.3 | 0.171 | 0.025 | 33 | 8527 | 8.24 | 58 |  | 175.97 | 3.5 | 6.85 | -3.852 | 0.24 | 101
8/17/2025 13:30 | 10 | 19 | 2.75 | 7.572 | 1.758 | 7.13 | 54 | 1.98 | 70.3 | 0.171 | 0.025 | 33 | 8527 | 8.24 | 58 |  | 180.74 | 3.44 | 6.84 | -3.852 | 0.23 | 101
8/17/2025 13:45 | 9 | 19 | 2.75 | 7.571 | 1.846 | 7.13 | 54 | 1.98 | 70.3 | 0.171 | 0.025 | 33 | 8527 | 8.23 | 58 |  | 180.65 | 3.44 | 6.82 | -3.852 | 0.24 | 101
8/17/2025 14:00 | 7 | 19 | 2.75 | 7.598 | 1.785 | 7.13 | 54 | 1.98 | 70.7 | 0.171 | 0.025 | 33 | 8527 | 8.22 | 57 |  | 180.21 | 3.42 | 6.83 | -3.852 | 0.24 | 101
8/17/2025 14:15 | 7 | 19 | 2.75 | 7.612 | 2.222 | 7.12 | 54 | 1.98 | 70.7 | 0.171 | 0.025 | 33 | 8527 | 8.21 | 57 |  | 180.81 | 3.42 | 6.8 | -3.852 | 0.21 | 101
8/17/2025 14:30 | 1 | 19 | 2.75 | 7.617 | 2.466 | 7.11 | 54 | 1.98 | 70.7 | 0.171 | 0.025 | 33 | 8527 | 8.21 | 57 |  | 180.15 | 3.41 | 6.79 | -3.852 | 0.2 | 101
8/17/2025 14:45 | 1 | 19 | 2.75 | 7.58 | 2.404 | 7.11 | 54 | 1.98 | 70.7 | 0.171 | 0.025 | 33 | 8527 | 8.21 | 57 |  | 180.54 | 3.43 | 6.84 | -3.852 | 0.21 | 101
8/17/2025 15:00 | 5 | 19 | 2.75 | 7.621 | 2.223 | 7.12 | 54 | 1.98 | 70.7 | 0.171 | 0.025 | 33 | 8527 | 8.21 | 57 |  | 180.3 | 3.41 | 6.86 | -3.852 | 0.23 | 101
8/17/2025 15:15 | 5 | 19 | 2.75 | 7.591 | 2.15 | 7.13 | 54 | 1.98 | 70.7 | 0.171 | 0.025 | 33 | 8527 | 8.2 | 57 |  | 180.82 | 3.43 | 6.87 | -3.852 | 0.23 | 101
8/17/2025 15:30 | 0 | 19 | 2.75 | 7.589 | 2.227 | 7.14 | 54 | 1.98 | 70.7 | 0.171 | 0.025 | 33 | 8527 | 8.19 | 57 |  | 180.05 | 3.42 | 6.87 | -3.852 | 0.23 | 101
8/17/2025 15:45 | -1 | 19 | 2.75 | 7.054 | 2.365 | 7.14 | 54 | 1.98 | 70.7 | 0.171 | 0.025 | 33 | 8527 | 8.18 | 57 |  | 171.88 | 3.51 | 6.86 | -3.852 | 0.22 | 101
8/17/2025 16:00 | 4 | 19 | 2.75 | 7.302 | 2.091 | 7.14 | 54 | 1.98 | 70.7 | 0.152 | 0.025 | 33 | 8527 | 8.17 | 57 |  | 178.51 | 3.52 | 6.86 | -3.852 | 0.23 | 101
8/17/2025 16:15 | -5 | 19 | 2.75 | 7.333 | 2.077 | 7.15 | 54 | 1.98 | 70.7 | 0.152 | 0.025 | 33 | 8527 | 8.16 | 57 |  | 178.22 | 3.5 | 6.87 | -3.852 | 0.23 | 101
8/17/2025 16:30 | -2 | 19 | 2.75 | 7.342 | 2.454 | 7.14 | 54 | 1.98 | 70.7 | 0.152 | 0.025 | 33 | 8527 | 8.15 | 57 |  | 178.39 | 3.5 | 6.85 | -3.852 | 0.2 | 101
8/17/2025 16:45 | 1 | 19 | 2.75 | 7.364 | 2.457 | 7.13 | 54 | 1.98 | 70.7 | 0.152 | 0.025 | 33 | 8527 | 8.15 | 57 |  | 178.76 | 3.5 | 6.84 | -3.852 | 0.21 | 101
8/17/2025 17:00 | 0 | 19 | 2.75 | 7.365 | 2.505 | 7.13 | 54 | 1.98 | 70.7 | 0.152 | 0.024 | 33 | 8527 | 8.14 | 57 |  | 178.42 | 3.49 | 6.84 | -3.852 | 0.22 | 101
8/17/2025 17:15 | 5 | 19 | 2.75 | 7.312 | 2.468 | 7.13 | 54 | 1.98 | 70.7 | 0.152 | 0.024 | 33 | 8527 | 8.15 | 57 |  | 178.12 | 3.51 | 6.84 | -3.852 | 0.22 | 101
8/17/2025 17:30 | 4 | 19 | 2.75 | 7.347 | 2.413 | 7.13 | 54 | 1.98 | 70.7 | 0.152 | 0.024 | 33 | 8527 | 8.15 | 57 |  | 178.03 | 3.49 | 6.83 | -3.852 | 0.23 | 101
8/17/2025 17:45 | 6 | 19 | 2.75 | 7.343 | 2.476 | 7.17 | 54 | 1.98 | 70.7 | 0.152 | 0.024 | 33 | 8527 | 8.16 | 57 |  | 76.75 | 1.51 | 6.84 | -3.852 | 0.23 | 101
8/17/2025 18:00 | -2 | 19 | 2.75 | 7.332 | 2.644 | 7.17 | 54 | 1.98 | 70.8 | 0.152 | 0.024 | 33 | 8527 | 8.16 | 57 |  | 76.31 | 1.5 | 6.84 | -3.852 | 0.22 | 101
8/17/2025 18:15 | 7 | 19 | 2.75 | 7.312 | 2.613 | 7.17 | 54 | 1.98 | 70.8 | 0.152 | 0.024 | 33 | 8527 | 8.17 | 57 |  | 76.63 | 1.51 | 6.82 | -3.852 | 0.21 | 101
8/17/2025 18:30 | 5 | 19 | 2.75 | 7.318 | 2.598 | 7.19 | 54 | 1.98 | 70.8 | 0.152 | 0.025 | 33 | 8527 | 8.18 | 57 |  | 76.23 | 1.5 | 6.85 | -3.852 | 0.22 | 101
8/17/2025 18:45 | -1 | 19 | 2.75 | 7.316 | 2.475 | 7.2 | 54 | 1.98 | 70.8 | 0.152 | 0.025 | 33 | 8527 | 8.19 | 57 |  | 76.03 | 1.5 | 6.87 | -3.852 | 0.22 | 101
8/17/2025 19:00 | 4 | 19 | 2.75 | 7.333 | 2.643 | 7.19 | 54 | 1.98 | 70.8 | 0.152 | 0.024 | 33 | 8527 | 8.2 | 57 |  | 76.04 | 1.49 | 6.86 | -3.852 | 0.23 | 101
8/17/2025 19:15 | 5 | 19 | 2.75 | 7.29 | 3.097 | 7.17 | 54 | 1.98 | 70.8 | 0.152 | 0.025 | 33 | 8527 | 8.2 | 57 |  | 76.23 | 1.51 | 6.83 | -3.852 | 0.21 | 101
8/17/2025 19:30 | 4 | 19 | 2.75 | 7.286 | 2.992 | 7.17 | 54 | 1.98 | 70.8 | 0.152 | 0.024 | 33 | 8527 | 8.2 | 57 |  | 76.15 | 1.51 | 6.82 | -3.852 | 0.22 | 101
8/17/2025 19:45 | -8 | 19 | 2.75 | 7.284 | 2.806 | 7.18 | 54 | 1.98 | 70.8 | 0.152 | 0.024 | 33 | 8527 | 8.21 | 57 |  | 76.29 | 1.51 | 6.83 | -3.852 | 0.22 | 101
8/17/2025 20:00 | 4 | 19 | 2.75 | 7.273 | 2.624 | 7.18 | 54 | 1.98 | 70.8 | 0.185 | 0.024 | 33 | 8527 | 8.22 | 57 |  | 160.43 | 3.18 | 6.84 | -3.852 | 0.22 | 101
8/17/2025 20:15 | 6 | 19 | 2.75 | 7.287 | 2.24 | 7.16 | 54 | 1.98 | 70.8 | 0.185 | 0.024 | 33 | 8527 | 8.23 | 57 |  | 177.37 | 3.51 | 6.84 | -3.852 | 0.22 | 101
8/17/2025 20:30 | -3 | 19 | 2.75 | 7.264 | 39.935 | 7.09 | 54 | 1.98 | 70.8 | 0.185 | 0.024 | 33 | 8527 | 8.24 | 57 |  | 176.16 | 3.49 | 6.82 | -3.852 | 0.27 | 101
8/17/2025 20:45 | -4 | 19 | 2.75 | 7.229 | 39.936 | 7.11 | 54 | 1.98 | 70.8 | 0.185 | 0.025 | 33 | 8527 | 8.24 | 57 |  | 0 | 0 | 6.81 | -3.852 | 0.23 | 101
8/17/2025 21:00 | 1 | 19 | 2.75 | 7.19 | 5.386 | 7.18 | 54 | 1.98 | 70.8 | 0.185 | 0.025 | 33 | 8527 | 8.25 | 57 |  | 0 | 0 | 6.81 | -3.852 | 0.22 | 101
8/17/2025 21:15 | 0 | 19 | 2.75 | 7.149 | 4.314 | 7.19 | 54 | 1.98 | 70.8 | 0.185 | 0.024 | 33 | 8527 | 8.25 | 57 |  | 0 | 0 | 6.83 | -3.852 | 0.22 | 101
8/17/2025 21:30 | 5 | 19 | 2.75 | 7.158 | 4.306 | 7.17 | 54 | 1.98 | 70.8 | 0.185 | 0.024 | 33 | 8527 | 8.25 | 57 |  | 0 | 0 | 6.8 | -3.852 | 0.21 | 101
8/17/2025 21:45 | 5 | 19 | 2.75 | 7.13 | 3.992 | 7.16 | 54 | 1.98 | 70.8 | 0.185 | 0.025 | 33 | 8527 | 8.24 | 57 |  | 0 | 0 | 6.79 | -3.852 | 0.21 | 101
8/17/2025 22:00 | 0 | 19 | 2.75 | 6.76 | 3.572 | 7.16 | 55 | 1.98 | 70.7 | 0.185 | 0.024 | 33 | 8527 | 8.24 | 57 |  | 0 | 0 | 6.78 | -3.852 | 0.21 | 101
8/17/2025 22:15 | 3 | 19 | 2.75 | 6.662 | 3.63 | 7.16 | 55 | 1.98 | 70.7 | 0.185 | 0.024 | 33 | 8527 | 8.23 | 57 |  | 0 | 0 | 6.78 | -3.852 | 0.2 | 101
8/17/2025 22:30 | 2 | 19 | 2.75 | 7.055 | 3.183 | 7.18 | 55 | 1.98 | 70.7 | 0.185 | 0.024 | 33 | 8527 | 8.22 | 57 |  | 0 | 0 | 6.81 | -3.852 | 0.23 | 101
8/17/2025 22:45 | 1 | 19 | 2.75 | 7.048 | 3.265 | 7.2 | 55 | 1.98 | 70.7 | 0.185 | 0.024 | 33 | 8527 | 8.22 | 57 |  | 0 | 0 | 6.85 | -3.852 | 0.21 | 101
8/17/2025 23:00 | 4 | 19 | 2.75 | 6.959 | 3.147 | 7.2 | 55 | 1.98 | 70.7 | 0.185 | 0.024 | 33 | 8527 | 8.22 | 57 |  | 0 | 0 | 6.85 | -3.852 | 0.22 | 101
8/17/2025 23:15 | 6 | 19 | 2.75 | 7.267 | 3.163 | 7.19 | 55 | 1.98 | 70.7 | 0.185 | 0.024 | 33 | 8527 | 8.21 | 57 |  | 169.73 | 3.36 | 6.83 | -3.852 | 0.22 | 101
8/17/2025 23:30 | 5 | 19 | 2.75 | 7.622 | 6.159 | 7.13 | 55 | 1.98 | 70.7 | 0.185 | 0.025 | 35.85 | 9159 | 8.2 | 57 |  | 177.18 | 3.35 | 6.81 | -3.852 | 0.23 | 101
8/17/2025 23:45 | 6 | 19 | 2.75 | 7.576 | 3.538 | 7.12 | 55 | 1.98 | 70.7 | 0.185 | 0.026 | 35.85 | 9159 | 8.19 | 57 |  | 177.17 | 3.37 | 6.82 | -3.852 | 0.22 | 101
8/18/2025 00:00 | 3 | 19 | 2.75 | 7.539 | 3.035 | 7.11 | 55 | 1.98 | 70.7 | 0.309 | 0.027 | 35.85 | 9159 | 8.2 | 57 |  | 177.19 | 3.38 | 6.82 | -3.852 | 0.21 | 101
8/18/2025 00:15 | 4 | 19 | 2.75 | 7.61 | 2.856 | 7.1 | 55 | 1.98 | 70.7 | 0.309 | 0.027 | 35.85 | 9159 | 8.2 | 57 |  | 177.31 | 3.36 | 6.82 | -3.852 | 0.22 | 101
8/18/2025 00:30 | -1 | 19 | 2.75 | 7.599 | 2.804 | 7.09 | 55 | 1.98 | 70.7 | 0.309 | 0.027 | 35.85 | 9159 | 8.19 | 57 |  | 177.38 | 3.36 | 6.82 | -3.852 | 0.2 | 101
8/18/2025 00:45 | 5 | 19 | 2.75 | 7.644 | 2.523 | 7.1 | 55 | 1.98 | 70.7 | 0.309 | 0.026 | 35.85 | 9159 | 8.17 | 57 |  | 176.91 | 3.33 | 6.82 | -3.852 | 0.23 | 101
8/18/2025 01:00 | 4 | 19 | 2.75 | 7.065 | 2.529 | 7.09 | 55 | 1.98 | 70.7 | 0.309 | 0.026 | 35.85 | 9159 | 8.18 | 57 |  | 171.86 | 3.5 | 6.83 | -3.852 | 0.22 | 101
8/18/2025 01:15 | 3 | 19 | 2.75 | 7.058 | 2.973 | 7.09 | 55 | 1.98 | 70.7 | 0.309 | 0.026 | 35.85 | 9159 | 8.2 | 57 |  | 171.34 | 3.5 | 6.82 | -3.852 | 0.21 | 101
8/18/2025 01:30 | 7 | 19 | 2.75 | 7.308 | 2.585 | 7.09 | 55 | 1.98 | 70.7 | 0.309 | 0.026 | 35.85 | 9159 | 8.23 | 57 |  | 176.5 | 3.48 | 6.82 | -3.852 | 0.21 | 101
8/18/2025 01:45 | 8 | 19 | 2.75 | 7.56 | 2.844 | 7.09 | 55 | 1.98 | 70.7 | 0.309 | 0.026 | 35.85 | 9159 | 8.24 | 57 |  | 176.83 | 3.37 | 6.83 | -3.852 | 0.21 | 101
8/18/2025 02:00 | 4 | 19 | 2.75 | 7.608 | 3.098 | 7.08 | 55 | 1.98 | 70.5 | 0.309 | 0.026 | 35.85 | 9159 | 8.24 | 58 |  | 176.9 | 3.35 | 6.83 | -3.852 | 0.19 | 101
8/18/2025 02:15 | 8 | 19 | 2.75 | 7.51 | 3.029 | 7.08 | 55 | 1.98 | 70.5 | 0.309 | 0.026 | 35.85 | 9159 | 8.24 | 58 |  | 177.57 | 3.4 | 6.82 | -3.852 | 0.21 | 101
8/18/2025 02:30 | 2 | 19 | 2.75 | 7.51 | 2.917 | 7.08 | 55 | 1.98 | 70.5 | 0.309 | 0.026 | 35.85 | 9159 | 8.24 | 58 |  | 176.91 | 3.39 | 6.83 | -3.852 | 0.19 | 101
8/18/2025 02:45 | 7 | 19 | 2.75 | 8.134 | 2.83 | 7.08 | 55 | 1.98 | 70.5 | 0.309 | 0.026 | 35.85 | 9159 | 8.23 | 58 |  | 176.53 | 3.13 | 6.83 | -3.852 | 0.21 | 101
8/18/2025 03:00 | 3 | 19 | 2.75 | 8.463 | 2.924 | 7.08 | 55 | 1.98 | 70.5 | 0.309 | 0.026 | 35.85 | 9159 | 8.23 | 58 |  | 177.09 | 3.01 | 6.82 | -3.852 | 0.19 | 101
8/18/2025 03:15 | 0 | 19 | 2.75 | 8.483 | 2.878 | 7.07 | 55 | 1.98 | 70.5 | 0.309 | 0.026 | 35.85 | 9159 | 8.23 | 58 |  | 176.91 | 3 | 6.81 | -3.852 | 0.19 | 101
8/18/2025 03:30 | 8 | 19 | 2.75 | 8.459 | 2.976 | 7.07 | 55 | 1.98 | 70.5 | 0.309 | 0.026 | 35.85 | 9159 | 8.23 | 58 |  | 176.67 | 3.01 | 6.79 | -3.852 | 0.18 | 101
8/18/2025 03:45 | 8 | 19 | 2.75 | 7.539 | 3.023 | 7.07 | 55 | 1.98 | 70.5 | 0.309 | 0.026 | 35.85 | 9159 | 8.23 | 58 |  | 158.35 | 3.02 | 6.79 | -3.852 | 0.22 | 101
8/18/2025 04:00 | 10 | 19 | 2.75 | 7.454 | 3.103 | 7.08 | 55 | 1.98 | 70.5 | 0.29 | 0.026 | 35.85 | 9159 | 8.23 | 58 |  | 179.9 | 3.48 | 6.79 | -3.852 | 0.22 | 101
8/18/2025 04:15 | 10 | 19 | 2.75 | 7.425 | 2.589 | 7.08 | 55 | 1.98 | 70.5 | 0.29 | 0.026 | 35.85 | 9159 | 8.24 | 58 |  | 180.01 | 3.49 | 6.79 | -3.852 | 0.19 | 101
8/18/2025 04:30 | 10 | 19 | 2.75 | 7.835 | 2.552 | 7.08 | 55 | 1.98 | 70.5 | 0.29 | 0.026 | 35.85 | 9159 | 8.26 | 58 |  | 179.59 | 3.3 | 6.8 | -3.852 | 0.19 | 101
8/18/2025 04:45 | 10 | 19 | 2.75 | 7.942 | 2.63 | 7.09 | 55 | 1.98 | 70.5 | 0.29 | 0.026 | 35.85 | 9159 | 8.29 | 58 |  | 179.23 | 3.25 | 6.8 | -3.852 | 0.2 | 101
8/18/2025 05:00 | 5 | 19 | 2.75 | 7.884 | 2.53 | 7.09 | 55 | 1.98 | 70.5 | 0.29 | 0.026 | 35.85 | 9159 | 8.3 | 58 |  | 179.94 | 3.29 | 6.81 | -3.852 | 0.18 | 101
8/18/2025 05:15 | 10 | 19 | 2.75 | 7.287 | 2.54 | 7.08 | 55 | 1.98 | 70.5 | 0.29 | 0.026 | 36.74 | 9184 | 8.3 | 58 |  | 177.23 | 3.5 | 6.81 | -3.852 | 0.2 | 101
8/18/2025 05:30 | 2 | 19 | 2.75 | 7.331 | 2.63 | 7.08 | 55 | 1.98 | 70.5 | 0.29 | 0.026 | 36.74 | 9184 | 8.29 | 58 |  | 179.24 | 3.52 | 6.8 | -3.852 | 0.18 | 101
8/18/2025 05:45 | 1 | 19 | 2.75 | 8.114 | 2.809 | 7.07 | 55 | 1.98 | 70.5 | 0.29 | 0.027 | 36.74 | 9184 | 8.27 | 58 |  | 179.32 | 3.18 | 6.79 | -3.852 | 0.22 | 101
8/18/2025 06:00 | 6 | 19 | 2.75 | 8.081 | 2.723 | 7.07 | 55 | 1.98 | 70.5 | 0.29 | 0.027 | 36.74 | 9184 | 8.25 | 58 |  | 179.28 | 3.19 | 6.79 | -3.852 | 0.19 | 101
8/18/2025 06:15 | 6 | 19 | 2.75 | 8.054 | 2.775 | 7.07 | 55 | 1.98 | 70.5 | 0.29 | 0.027 | 36.74 | 9184 | 8.2 | 58 |  | 179.54 | 3.21 | 6.79 | -3.852 | 0.19 | 101
8/18/2025 06:30 | -2 | 19 | 2.75 | 8.107 | 2.827 | 7.07 | 55 | 1.98 | 70.5 | 0.29 | 0.026 | 36.74 | 9184 | 8.16 | 58 |  | 179.39 | 3.19 | 6.79 | -3.852 | 0.19 | 101
8/18/2025 06:45 | 4 | 19 | 2.75 | 8.072 | 2.801 | 7.07 | 55 | 1.98 | 70.5 | 0.29 | 0.026 | 36.74 | 9184 | 8.16 | 58 |  | 180 | 3.21 | 6.8 | -3.852 | 0.19 | 101
8/18/2025 07:00 | -19 | 19 | 2.75 | 8.06 | 2.845 | 7.07 | 55 | 1.98 | 70.5 | 0.29 | 0.026 | 36.74 | 9184 | 8.17 | 58 |  | 178.64 | 3.19 | 6.8 | -3.852 | 0.22 | 98
8/18/2025 07:15 | 3 | 19 | 2.75 | 8.092 | 2.779 | 7.07 | 55 | 1.98 | 70.5 | 0.29 | 0.026 | 36.74 | 9184 | 8.19 | 58 |  | 179.62 | 3.2 | 6.8 | -3.852 | 0.18 | 101
8/18/2025 07:30 | 5 | 19 | 2.75 | 8.047 | 2.75 | 7.08 | 55 | 1.98 | 70.5 | 0.29 | 0.026 | 36.74 | 9184 | 8.21 | 58 |  | 178.72 | 3.2 | 6.8 | -3.852 | 0.19 | 101
8/18/2025 07:45 | -17 | 19 | 2.75 | 8.032 | 2.903 | 7.09 | 55 | 1.98 | 70.5 | 0.29 | 0.026 | 36.74 | 9184 | 8.21 | 58 |  | 179.36 | 3.22 | 6.81 | -3.852 | 0.2 | 101
8/18/2025 08:00 | -1 | 19 | 2.75 | 8.013 | 2.795 | 7.09 | 55 | 1.98 | 70.5 | 0.284 | 0.026 | 36.74 | 9184 | 8.21 | 58 |  | 179.35 | 3.22 | 6.81 | -3.852 | 0.19 | 101
8/18/2025 08:15 | 1 | 19 | 2.75 | 8.053 | 2.904 | 7.09 | 55 | 1.98 | 70.5 | 0.284 | 0.026 | 36.74 | 9184 | 8.21 | 58 |  | 179.07 | 3.2 | 6.82 | -3.852 | 0.26 | 101
8/18/2025 08:30 | 1 | 19 | 2.75 | 8.051 | 2.867 | 7.09 | 55 | 1.98 | 70.5 | 0.284 | 0.026 | 36.74 | 9184 | 8.2 | 58 |  | 179.38 | 3.21 | 6.83 | -3.852 | 0.18 | 101
8/18/2025 08:45 | 4 | 19 | 2.75 | 8.02 | 2.826 | 7.09 | 55 | 1.98 | 70.5 | 0.284 | 0.025 | 36.74 | 9184 | 8.2 | 58 |  | 179.29 | 3.22 | 6.83 | -3.852 | 0.18 | 101
8/18/2025 09:00 | 0 | 19 | 2.75 | 8.055 | 2.787 | 7.09 | 55 | 1.98 | 70.5 | 0.284 | 0.025 | 36.74 | 9184 | 8.19 | 58 |  | 178.65 | 3.19 | 6.83 | -3.852 | 0.21 | 101
8/18/2025 09:15 | 3 | 19 | 2.75 | 7.997 | 2.711 | 7.09 | 55 | 1.98 | 70.5 | 0.284 | 0.025 | 36.74 | 9184 | 8.19 | 58 |  | 177.87 | 3.2 | 6.83 | -3.852 | 0.19 | 101
8/18/2025 09:30 | 5 | 19 | 2.75 | 8.09 | 25.215 | 7.08 | 55 | 1.98 | 70.5 | 0.284 | 0.025 | 36.74 | 9184 | 8.18 | 58 |  | 177.34 | 3.16 | 6.83 | -3.852 | 0.2 | 101
8/18/2025 09:45 | 4 | 19 | 2.75 | 8.092 | 4.262 | 7.08 | 55 | 1.98 | 70.5 | 0.284 | 0.025 | 36.74 | 9184 | 8.18 | 58 |  | 177.68 | 3.16 | 6.83 | -3.852 | 0.19 | 101
8/18/2025 10:00 | 6 | 19 | 2.75 | 7.72 | 3.215 | 7.07 | 53 | 1.98 | 70.5 | 0.284 | 0.025 | 36.74 | 9184 | 8.18 | 58 |  | 177.08 | 3.3 | 6.83 | -3.852 | 0.2 | 101
8/18/2025 10:15 | 7 | 19 | 2.75 | 7.547 | 3.043 | 7.07 | 53 | 1.98 | 70.5 | 0.284 | 0.025 | 36.74 | 9184 | 8.18 | 58 |  | 177.39 | 3.38 | 6.82 | -3.852 | 0.18 | 101
8/18/2025 10:30 | 6 | 19 | 2.75 | 7.964 | 2.865 | 7.08 | 53 | 1.98 | 70.5 | 0.284 | 0.025 | 36.74 | 9184 | 8.18 | 58 |  | 177.46 | 3.21 | 6.82 | -3.852 | 0.18 | 101
8/18/2025 10:45 | 5 | 19 | 2.75 | 8.222 | 2.819 | 7.08 | 53 | 1.98 | 70.5 | 0.284 | 0.025 | 36.74 | 9184 | 8.18 | 58 |  | 177.33 | 3.11 | 6.82 | -3.852 | 0.17 | 101
8/18/2025 11:00 | 7 | 19 | 2.75 | 8.211 | 2.829 | 7.08 | 53 | 1.98 | 70.5 | 0.284 | 0.025 | 36.74 | 9184 | 8.18 | 58 |  | 177.12 | 3.11 | 6.81 | -3.852 | 0.18 | 101
8/18/2025 11:15 | 5 | 19 | 2.75 | 8.198 | 2.848 | 7.08 | 53 | 1.98 | 70.5 | 0.284 | 0.025 | 36.74 | 9184 | 8.18 | 58 |  | 177.38 | 3.12 | 6.82 | -3.852 | 0.18 | 101
8/18/2025 11:30 | 7 | 19 | 2.75 | 8.19 | 2.672 | 7.09 | 53 | 1.98 | 70.5 | 0.284 | 0.025 | 36.74 | 9184 | 8.32 | 58 |  | 178.03 | 3.13 | 6.82 | -3.852 | 0.18 | 101
8/18/2025 11:45 | 7 | 19 | 2.75 | 7.959 | 2.797 | 7.09 | 53 | 1.98 | 70.5 | 0.284 | 0.025 | 36.74 | 9184 | 8.34 | 58 |  | 177.66 | 3.21 | 6.83 | -3.852 | 0.17 | 101
8/18/2025 12:00 | 9 | 19 | 2.75 | 7.731 | 2.703 | 7.09 | 53 | 1.98 | 70.5 | 0.153 | 0.025 | 36.74 | 9184 | 8.35 | 58 |  | 177.27 | 3.3 | 6.8 | -3.852 | 0.18 | 101
8/18/2025 12:15 | -2 | 19 | 2.75 | 7.816 | 8.831 | 7.05 | 53 | 1.98 | 70.5 | 0.153 | 0.025 | 36.74 | 9184 | 8.35 | 58 |  | 177.68 | 3.27 | 6.76 | -3.852 | 0.23 | 101
8/18/2025 12:30 | 9 | 19 | 2.75 | 7.817 | 2.073 | 7.08 | 53 | 1.98 | 70.5 | 0.153 | 0.025 | 36.74 | 9184 | 8.35 | 58 |  | 177.35 | 3.27 | 6.75 | -3.852 | 0.25 | 101
8/18/2025 12:45 | 11 | 19 | 2.75 | 7.804 | 2.114 | 7.12 | 53 | 1.98 | 70.5 | 0.153 | 0.025 | 36.74 | 9184 | 8.35 | 58 |  | 81.67 | 1.51 | 6.84 | -3.852 | 0.23 | 101
8/18/2025 13:00 | 11 | 19 | 2.75 | 7.98 | 2.04 | 7.14 | 53 | 1.98 | 70.5 | 0.153 | 0.025 | 36.74 | 9184 | 8.35 | 58 |  | 83.08 | 1.5 | 6.86 | -3.852 | 0.23 | 101
8/18/2025 13:15 | 12 | 19 | 2.75 | 8.044 | 2.062 | 7.15 | 53 | 1.98 | 70.5 | 0.153 | 0.025 | 36.74 | 9184 | 8.34 | 58 |  | 82.94 | 1.48 | 6.86 | -3.852 | 0.23 | 101
8/18/2025 13:30 | 10 | 19 | 2.75 | 8.205 | 2.289 | 7.14 | 53 | 1.98 | 70.5 | 0.153 | 0.025 | 36.74 | 9184 | 8.34 | 58 |  | 85.3 | 1.5 | 6.84 | -3.852 | 0.24 | 101
8/18/2025 13:45 | 11 | 19 | 2.75 | 8.146 | 2.242 | 7.14 | 53 | 1.98 | 70.5 | 0.153 | 0.025 | 38.16 | 9376 | 8.33 | 58 |  | 85.05 | 1.5 | 6.84 | -3.852 | 0.23 | 101
8/18/2025 14:00 | 9 | 19 | 2.75 | 8.21 | 2.395 | 7.13 | 53 | 1.98 | 70.8 | 0.153 | 0.026 | 38.16 | 9376 | 8.32 | 56 |  | 85.66 | 1.5 | 6.83 | -3.852 | 0.23 | 101
8/18/2025 14:15 | 12 | 19 | 2.75 | 7.58 | 2.38 | 7.13 | 53 | 1.98 | 70.8 | 0.153 | 0.026 | 38.16 | 9376 | 8.32 | 56 |  | 79.02 | 1.5 | 6.83 | -3.852 | 0.24 | 101
8/18/2025 14:30 | 10 | 19 | 2.75 | 7.573 | 2.592 | 7.13 | 53 | 1.98 | 70.8 | 0.153 | 0.026 | 38.16 | 9376 | 8.31 | 56 |  | 78.83 | 1.5 | 6.83 | -3.852 | 0.23 | 101
8/18/2025 14:45 | 11 | 19 | 2.75 | 7.608 | 2.763 | 7.12 | 53 | 1.98 | 70.8 | 0.153 | 0.026 | 38.16 | 9376 | 8.29 | 56 |  | 79.19 | 1.5 | 6.81 | -3.852 | 0.23 | 101
8/18/2025 15:00 | 5 | 19 | 2.75 | 7.781 | 2.8 | 7.11 | 53 | 1.98 | 70.8 | 0.153 | 0.026 | 38.16 | 9376 | 8.28 | 56 |  | 81.29 | 1.5 | 6.81 | -3.852 | 0.24 | 101
8/18/2025 15:15 | 7 | 19 | 2.75 | 7.83 | 2.816 | 7.12 | 53 | 1.98 | 70.8 | 0.153 | 0.026 | 38.16 | 9376 | 8.29 | 56 |  | 81.06 | 1.49 | 6.81 | -3.852 | 0.24 | 101
8/18/2025 15:30 | 7 | 19 | 2.75 | 7.767 | 2.651 | 7.13 | 53 | 1.98 | 70.8 | 0.153 | 0.026 | 38.16 | 9376 | 8.31 | 56 |  | 80.71 | 1.5 | 6.82 | -3.852 | 0.24 | 101
8/18/2025 15:45 | 9 | 19 | 2.75 | 7.743 | 2.552 | 7.14 | 53 | 1.98 | 70.8 | 0.153 | 0.026 | 38.16 | 9376 | 8.35 | 56 |  | 80.95 | 1.51 | 6.83 | -3.852 | 0.24 | 101
8/18/2025 16:00 | 8 | 19 | 2.75 | 7.694 | 2.554 | 7.14 | 53 | 1.98 | 70.8 | 0.164 | 0.026 | 38.16 | 9376 | 8.35 | 56 |  | 80.91 | 1.51 | 6.83 | -3.852 | 0.24 | 101
8/18/2025 16:15 | 10 | 19 | 2.75 | 7.437 | 2.597 | 7.15 | 53 | 1.98 | 70.8 | 0.164 | 0.026 | 38.16 | 9376 | 8.35 | 56 |  | 77.8 | 1.51 | 6.84 | -3.852 | 0.23 | 101
8/18/2025 16:30 | 10 | 19 | 2.75 | 7.768 | 2.757 | 7.15 | 53 | 1.98 | 70.8 | 0.164 | 0.025 | 38.16 | 9376 | 8.35 | 56 |  | 80.57 | 1.49 | 6.83 | -3.852 | 0.23 | 101
8/18/2025 16:45 | 7 | 19 | 2.75 | 7.73 | 2.767 | 7.16 | 53 | 1.98 | 70.8 | 0.164 | 0.025 | 38.16 | 9376 | 8.34 | 56 |  | 80.58 | 1.5 | 6.84 | -3.852 | 0.24 | 101
8/18/2025 17:00 | 8 | 19 | 2.75 | 7.738 | 2.519 | 7.18 | 53 | 1.98 | 70.8 | 0.164 | 0.025 | 38.16 | 9376 | 8.34 | 56 |  | 80.27 | 1.49 | 6.85 | -3.852 | 0.22 | 101
8/18/2025 17:15 | 10 | 19 | 2.75 | 7.708 | 2.938 | 7.18 | 53 | 1.98 | 70.8 | 0.164 | 0.025 | 38.16 | 9376 | 8.34 | 56 |  | 80.56 | 1.51 | 6.86 | -3.852 | 0.23 | 101
8/18/2025 17:30 | 7 | 19 | 2.75 | 7.314 | 2.529 | 7.18 | 53 | 1.98 | 70.8 | 0.164 | 0.025 | 38.16 | 9376 | 8.34 | 56 |  | 76.27 | 1.5 | 6.85 | -3.852 | 0.21 | 101
8/18/2025 17:45 | 10 | 19 | 2.75 | 7.375 | 2.669 | 7.17 | 53 | 1.98 | 70.8 | 0.164 | 0.025 | 38.16 | 9376 | 8.35 | 56 |  | 76.34 | 1.49 | 6.84 | -3.852 | 0.21 | 101
8/18/2025 18:00 | 9 | 19 | 2.75 | 7.671 | 2.569 | 7.17 | 53 | 1.98 | 71 | 0.164 | 0.025 | 38.16 | 9376 | 8.35 | 56 |  | 79.88 | 1.5 | 6.83 | -3.852 | 0.22 | 101
8/18/2025 18:15 | 10 | 19 | 2.75 | 7.699 | 2.767 | 7.15 | 53 | 1.98 | 71 | 0.164 | 0.025 | 38.16 | 9376 | 8.36 | 56 |  | 80.55 | 1.51 | 6.81 | -3.852 | 0.21 | 101
8/18/2025 18:30 | 10 | 19 | 2.75 | 7.703 | 3.228 | 7.12 | 53 | 1.98 | 71 | 0.164 | 0.025 | 38.16 | 9376 | 8.37 | 56 |  | 80.12 | 1.5 | 6.78 | -3.852 | 0.19 | 101
8/18/2025 18:45 | 12 | 19 | 2.75 | 7.733 | 3.068 | 7.14 | 53 | 1.98 | 71 | 0.164 | 0.025 | 38.16 | 9376 | 8.38 | 56 |  | 80.56 | 1.5 | 6.79 | -3.852 | 0.21 | 101
8/18/2025 19:00 | 11 | 19 | 2.75 | 7.223 | 2.36 | 7.19 | 53 | 1.98 | 71 | 0.164 | 0.025 | 38.16 | 9376 | 8.39 | 56 |  | 75.72 | 1.51 | 6.85 | -3.852 | 0.23 | 101
8/18/2025 19:15 | 8 | 19 | 2.75 | 7.316 | 2.063 | 7.22 | 53 | 1.98 | 71 | 0.164 | 0.026 | 38.16 | 9376 | 8.4 | 56 |  | 76.33 | 1.5 | 6.89 | -3.852 | 0.21 | 101
8/18/2025 19:30 | 4 | 19 | 2.75 | 7.755 | 2.706 | 7.22 | 53 | 1.98 | 71 | 0.164 | 0.026 | 38.16 | 9376 | 8.4 | 56 |  | 80.31 | 1.49 | 6.88 | -3.852 | 0.21 | 101
8/18/2025 19:45 | 7 | 19 | 2.75 | 8.022 | 3.417 | 7.14 | 53 | 1.98 | 71 | 0.164 | 0.026 | 38.16 | 9376 | 8.41 | 56 |  | 83.07 | 1.49 | 6.8 | -3.852 | 0.2 | 101
8/18/2025 20:00 | 9 | 19 | 2.75 | 8.001 | 3.284 | 7.14 | 53 | 1.98 | 71 | 0.217 | 0.026 | 38.74 | 9340 | 8.42 | 56 |  | 83.28 | 1.5 | 6.79 | -3.852 | 0.23 | 101
8/18/2025 20:15 | 9 | 19 | 2.75 | 7.244 | 2.982 | 7.16 | 53 | 1.98 | 71 | 0.217 | 0.027 | 38.74 | 9340 | 8.43 | 56 |  | 75.77 | 1.51 | 6.8 | -3.852 | 0.22 | 101
8/18/2025 20:30 | 9 | 19 | 2.75 | 7.724 | 3.129 | 7.15 | 53 | 1.98 | 71 | 0.217 | 0.027 | 38.74 | 9340 | 8.43 | 56 |  | 79.64 | 1.48 | 6.79 | -3.852 | 0.2 | 101
8/18/2025 20:45 | 8 | 19 | 2.75 | 7.614 | 3.008 | 7.14 | 53 | 1.98 | 71 | 0.217 | 0.027 | 38.74 | 9340 | 8.43 | 56 |  | 79.89 | 1.51 | 6.78 | -3.852 | 0.21 | 101
8/18/2025 21:00 | 9 | 19 | 2.75 | 7.142 | 2.732 | 7.15 | 53 | 1.98 | 71 | 0.217 | 0.027 | 38.74 | 9340 | 8.42 | 56 |  | 74.09 | 1.49 | 6.8 | -3.852 | 0.21 | 101
8/18/2025 21:15 | 9 | 19 | 2.75 | 7.1 | 2.495 | 7.17 | 53 | 1.98 | 71 | 0.217 | 0.027 | 38.74 | 9340 | 8.41 | 56 |  | 74.5 | 1.51 | 6.83 | -3.852 | 0.22 | 101
8/18/2025 21:30 | 9 | 19 | 2.75 | 7.455 | 2.421 | 7.18 | 53 | 1.98 | 71 | 0.217 | 0.027 | 38.74 | 9340 | 8.42 | 56 |  | 77.61 | 1.5 | 6.84 | -3.852 | 0.22 | 101
8/18/2025 21:45 | 9 | 19 | 2.75 | 7.432 | 2.231 | 7.2 | 53 | 1.98 | 71 | 0.217 | 0.027 | 38.74 | 9340 | 8.46 | 56 |  | 77.93 | 1.51 | 6.86 | -3.852 | 0.21 | 101
8/18/2025 22:00 | 10 | 19 | 2.75 | 7.431 | 2.106 | 7.21 | 55 | 1.98 | 70.8 | 0.217 | 0.027 | 38.74 | 9340 | 8.5 | 56 |  | 77.67 | 1.51 | 6.87 | -3.852 | 0.22 | 101
8/18/2025 22:15 | 6 | 19 | 2.75 | 6.985 | 2.012 | 7.22 | 55 | 1.98 | 70.8 | 0.217 | 0.027 | 38.74 | 9340 | 8.51 | 56 |  | 72.72 | 1.5 | 6.87 | -3.852 | 0.21 | 101
8/18/2025 22:30 | 6 | 19 | 2.75 | 7.009 | 2.026 | 7.18 | 55 | 1.98 | 70.8 | 0.217 | 0.027 | 38.74 | 9340 | 8.51 | 56 |  | 170.84 | 3.51 | 6.85 | -3.852 | 0.2 | 101
8/18/2025 22:45 | 7 | 19 | 2.75 | 7.411 | 2.071 | 7.17 | 55 | 1.98 | 70.8 | 0.217 | 0.026 | 38.74 | 9340 | 8.52 | 56 |  | 180.17 | 3.5 | 6.83 | -3.852 | 0.21 | 101
8/18/2025 23:00 | 8 | 19 | 2.75 | 7.397 | 2.264 | 7.15 | 55 | 1.98 | 70.8 | 0.217 | 0.026 | 38.74 | 9340 | 8.52 | 56 |  | 180.2 | 3.51 | 6.81 | -3.852 | 0.21 | 101
8/18/2025 23:15 | 9 | 19 | 2.75 | 6.974 | 2.497 | 7.15 | 55 | 1.98 | 70.8 | 0.217 | 0.026 | 38.74 | 9340 | 8.52 | 56 |  | 169.65 | 3.5 | 6.8 | -3.852 | 0.2 | 101
8/18/2025 23:30 | 11 | 19 | 2.75 | 7.002 | 39.936 | 7.08 | 55 | 1.98 | 70.8 | 0.217 | 0.026 | 38.74 | 9340 | 8.51 | 56 |  | 170.76 | 3.51 | 6.79 | -3.852 | 0.34 | 101
8/18/2025 23:45 | 2 | 19 | 2.75 | 8.301 | 39.937 | 7.07 | 55 | 1.98 | 70.8 | 0.217 | 0.026 | 38.87 | 9217 | 8.49 | 56 |  | 177.84 | 3.09 | 6.8 | -3.852 | 0.41 | 101
8/19/2025 00:00 | 5 | 19 | 2.75 | 8.153 | 39.937 | 7.09 | 55 | 1.98 | 70.8 | 0.218 | 0.027 | 38.87 | 9217 | 8.5 | 56 |  | 0 | 0 | 6.8 | -3.852 | 0.29 | 101
8/19/2025 00:15 | 6 | 19 | 2.75 | 7.582 | 5.969 | 7.15 | 55 | 1.98 | 70.8 | 0.218 | 0.028 | 38.87 | 9217 | 8.5 | 56 |  | 0 | 0 | 6.82 | -3.852 | 0.23 | 101
8/19/2025 00:30 | 7 | 19 | 2.75 | 7.575 | 4.023 | 7.18 | 55 | 1.98 | 70.8 | 0.218 | 0.028 | 38.87 | 9217 | 8.49 | 56 |  | 0 | 0 | 6.83 | -3.852 | 0.23 | 101
8/19/2025 00:45 | 7 | 19 | 2.75 | 8.009 | 3.375 | 7.18 | 55 | 1.98 | 70.8 | 0.218 | 0.028 | 38.87 | 9217 | 8.48 | 56 |  | 0 | 0 | 6.84 | -3.852 | 0.24 | 101
8/19/2025 01:00 | 9 | 19 | 2.75 | 7.962 | 2.925 | 7.19 | 55 | 1.98 | 70.8 | 0.218 | 0.028 | 38.87 | 9217 | 8.47 | 56 |  | 0 | 0 | 6.84 | -3.852 | 0.23 | 101
8/19/2025 01:15 | 8 | 19 | 2.75 | 7.972 | 37.725 | 7.16 | 55 | 1.98 | 70.8 | 0.218 | 0.027 | 38.87 | 9217 | 8.49 | 56 |  | 82.63 | 1.49 | 6.84 | -3.852 | 0.29 | 101
8/19/2025 01:30 | 8 | 19 | 2.75 | 7.476 | 8.938 | 7.14 | 55 | 1.98 | 70.8 | 0.218 | 0.027 | 38.87 | 9217 | 8.53 | 56 |  | 78.4 | 1.51 | 6.83 | -3.852 | 0.24 | 101
8/19/2025 01:45 | 10 | 19 | 2.75 | 7.845 | 4.478 | 7.14 | 55 | 1.98 | 70.8 | 0.218 | 0.027 | 38.87 | 9217 | 8.55 | 56 |  | 178.01 | 3.27 | 6.83 | -3.852 | 0.24 | 101
8/19/2025 02:00 | 8 | 19 | 2.75 | 8.079 | 3.597 | 7.13 | 55 | 1.98 | 70.8 | 0.218 | 0.027 | 38.87 | 9217 | 8.55 | 57 |  | 178.13 | 3.17 | 6.82 | -3.852 | 0.24 | 101
8/19/2025 02:15 | 10 | 19 | 2.75 | 7.996 | 3.499 | 7.11 | 55 | 1.98 | 70.8 | 0.218 | 0.027 | 38.87 | 9217 | 8.54 | 57 |  | 178.16 | 3.21 | 6.81 | -3.852 | 0.22 | 101
8/19/2025 02:30 | 8 | 19 | 2.75 | 8.127 | 3.177 | 7.1 | 55 | 1.98 | 70.8 | 0.218 | 0.028 | 38.87 | 9217 | 8.53 | 57 |  | 178.13 | 3.16 | 6.81 | -3.852 | 0.2 | 101
8/19/2025 02:45 | 9 | 19 | 2.75 | 8.105 | 3.124 | 7.1 | 55 | 1.98 | 70.8 | 0.218 | 0.028 | 38.87 | 9217 | 8.51 | 57 |  | 177.86 | 3.16 | 6.81 | -3.852 | 0.23 | 101
8/19/2025 03:00 | 10 | 19 | 2.75 | 8.069 | 2.989 | 7.1 | 55 | 1.98 | 70.8 | 0.218 | 0.028 | 38.87 | 9217 | 8.48 | 57 |  | 177.82 | 3.17 | 6.81 | -3.852 | 0.22 | 101
8/19/2025 03:15 | 10 | 19 | 2.75 | 8.099 | 3.199 | 7.11 | 55 | 1.98 | 70.8 | 0.218 | 0.028 | 38.87 | 9217 | 8.45 | 57 |  | 177.4 | 3.15 | 6.82 | -3.852 | 0.21 | 101
8/19/2025 03:30 | 8 | 19 | 2.75 | 7.798 | 3.181 | 7.11 | 55 | 1.98 | 70.8 | 0.218 | 0.028 | 38.87 | 9217 | 8.43 | 57 |  | 178.17 | 3.29 | 6.82 | -3.852 | 0.21 | 101
8/19/2025 03:45 | 5 | 19 | 2.75 | 7.683 | 2.971 | 7.1 | 55 | 1.98 | 70.8 | 0.218 | 0.028 | 38.87 | 9217 | 8.42 | 57 |  | 177.72 | 3.33 | 6.82 | -3.852 | 0.21 | 101
8/19/2025 04:00 | 8 | 19 | 2.75 | 8.108 | 3.13 | 7.1 | 55 | 1.98 | 70.8 | 0.29 | 0.028 | 38.87 | 9217 | 8.41 | 57 |  | 177.87 | 3.16 | 6.82 | -3.852 | 0.22 | 101
8/19/2025 04:15 | 9 | 19 | 2.75 | 8.105 | 3.075 | 7.1 | 55 | 1.98 | 70.8 | 0.29 | 0.027 | 38.87 | 9217 | 8.41 | 57 |  | 178.15 | 3.17 | 6.82 | -3.852 | 0.21 | 101
8/19/2025 04:30 | 8 | 19 | 2.75 | 8.037 | 3.005 | 7.11 | 55 | 1.98 | 70.8 | 0.29 | 0.027 | 38.87 | 9217 | 8.4 | 57 |  | 177.69 | 3.18 | 6.82 | -3.852 | 0.22 | 101
8/19/2025 04:45 | 9 | 19 | 2.75 | 8.077 | 2.894 | 7.11 | 55 | 1.98 | 70.8 | 0.29 | 0.027 | 38.87 | 9217 | 8.4 | 57 |  | 177.38 | 3.16 | 6.83 | -3.852 | 0.21 | 101
8/19/2025 05:00 | 9 | 19 | 2.75 | 7.689 | 2.854 | 7.11 | 55 | 1.98 | 70.8 | 0.29 | 0.027 | 38.87 | 9217 | 8.41 | 57 |  | 177.42 | 3.32 | 6.83 | -3.852 | 0.22 | 101
8/19/2025 05:15 | 8 | 19 | 2.75 | 7.702 | 2.921 | 7.11 | 55 | 1.98 | 70.8 | 0.29 | 0.027 | 38.87 | 9217 | 8.4 | 57 |  | 177.04 | 3.31 | 6.83 | -3.852 | 0.21 | 101
8/19/2025 05:30 | 9 | 19 | 2.75 | 8.023 | 2.887 | 7.1 | 55 | 1.98 | 70.8 | 0.29 | 0.027 | 38.87 | 9217 | 8.41 | 57 |  | 176.86 | 3.17 | 6.82 | -3.852 | 0.23 | 101
8/19/2025 05:45 | 8 | 19 | 2.75 | 7.981 | 2.837 | 7.1 | 55 | 1.98 | 70.8 | 0.29 | 0.027 | 38.87 | 9217 | 8.4 | 57 |  | 177.65 | 3.21 | 6.82 | -3.852 | 0.23 | 101
8/19/2025 06:00 | 9 | 19 | 2.75 | 8.016 | 2.916 | 7.1 | 55 | 1.98 | 70.8 | 0.29 | 0.027 | 38.87 | 9217 | 8.4 | 57 |  | 177.35 | 3.19 | 6.82 | -3.852 | 0.21 | 101
8/19/2025 06:15 | 8 | 19 | 2.75 | 7.634 | 2.845 | 7.1 | 55 | 1.98 | 70.8 | 0.29 | 0.027 | 38.87 | 9217 | 8.41 | 57 |  | 177.64 | 3.35 | 6.82 | -3.852 | 0.21 | 101
8/19/2025 06:30 | 9 | 19 | 2.75 | 7.679 | 2.938 | 7.15 | 55 | 1.98 | 70.8 | 0.29 | 0.026 | 38.87 | 9217 | 8.4 | 57 |  | 177.14 | 3.32 | 6.82 | -3.852 | 0.22 | 101
8/19/2025 06:45 | 7 | 19 | 2.75 | 7.865 | 2.134 | 7.07 | 55 | 1.98 | 70.8 | 0.29 | 0.026 | 38.87 | 9217 | 8.41 | 57 |  | 177.01 | 3.24 | 6.82 | -3.852 | 0.21 | 101
8/19/2025 07:00 | 7 | 19 | 2.75 | 8.014 | 2.207 | 7.1 | 55 | 1.98 | 70.8 | 0.29 | 0.026 | 38.87 | 9217 | 8.39 | 57 |  | 177.21 | 3.18 | 6.81 | -3.852 | 0.21 | 101
8/19/2025 07:15 | 8 | 19 | 2.75 | 8.031 | 2.182 | 7.11 | 55 | 1.98 | 70.8 | 0.29 | 0.026 | 38.87 | 9217 | 8.4 | 57 |  | 177.16 | 3.18 | 6.81 | -3.852 | 0.21 | 101
8/19/2025 07:30 | 8 | 19 | 2.75 | 8.026 | 2.267 | 7.12 | 55 | 1.98 | 70.8 | 0.29 | 0.026 | 38.87 | 9217 | 8.39 | 57 |  | 176.85 | 3.17 | 6.81 | -3.852 | 0.21 | 101
8/19/2025 07:45 | 2 | 19 | 2.75 | 7.435 | 2.425 | 7.12 | 55 | 1.98 | 70.8 | 0.29 | 0.026 | 38.87 | 9217 | 8.4 | 57 |  | 177.19 | 3.43 | 6.84 | -3.852 | 0.2 | 101
8/19/2025 08:00 | 9 | 19 | 2.75 | 7.387 | 2.357 | 7.12 | 55 | 1.98 | 70.8 | 0.279 | 0.026 | 38.87 | 9217 | 8.39 | 57 |  | 176.51 | 3.44 | 6.79 | -3.852 | 0.21 | 101
8/19/2025 08:15 | 8 | 19 | 2.75 | 8.066 | 2.335 | 7.13 | 55 | 1.98 | 70.8 | 0.279 | 0.026 | 38.87 | 9217 | 8.39 | 57 |  | 176.1 | 3.14 | 6.82 | -3.852 | 0.21 | 101
8/19/2025 08:30 | 6 | 19 | 2.75 | 8.05 | 2.502 | 7.13 | 55 | 1.98 | 70.8 | 0.279 | 0.026 | 38.87 | 9217 | 8.39 | 57 |  | 176.45 | 3.16 | 6.88 | -3.852 | 0.21 | 101
8/19/2025 08:45 | 6 | 19 | 2.75 | 8.066 | 2.412 | 7.13 | 55 | 1.98 | 70.8 | 0.279 | 0.026 | 38.87 | 9217 | 8.39 | 57 |  | 176.67 | 3.15 | 6.89 | -3.852 | 0.21 | 101
8/19/2025 09:00 | 7 | 19 | 2.75 | 8.023 | 2.381 | 7.13 | 55 | 1.98 | 70.8 | 0.279 | 0.025 | 38.87 | 9217 | 8.38 | 57 |  | 176.48 | 3.17 | 6.88 | -3.852 | 0.21 | 101
8/19/2025 09:15 | 7 | 19 | 2.75 | 7.951 | 2.261 | 7.13 | 55 | 1.98 | 70.8 | 0.279 | 0.025 | 38.87 | 9217 | 8.38 | 57 |  | 176.63 | 3.2 | 6.87 | -3.852 | 0.21 | 101
8/19/2025 09:30 | 8 | 19 | 2.75 | 8.001 | 2.168 | 7.13 | 55 | 1.98 | 70.8 | 0.279 | 0.025 | 38.87 | 9217 | 8.39 | 57 |  | 176.25 | 3.17 | 6.86 | -3.852 | 0.21 | 101
8/19/2025 09:45 | 9 | 19 | 2.75 | 8.007 | 2.144 | 7.13 | 55 | 1.98 | 70.8 | 0.279 | 0.025 | 38.87 | 9217 | 8.38 | 57 |  | 176.63 | 3.18 | 6.84 | -3.852 | 0.22 | 101
8/19/2025 10:00 | 8 | 19 | 2.75 | 7.735 | 1.982 | 7.13 | 56 | 1.98 | 70.8 | 0.279 | 0.025 | 38.87 | 9217 | 8.39 | 57 |  | 0 | 0 | 6.83 | -3.852 | 0.22 | 101
8/19/2025 10:15 | 9 | 19 | 2.75 | 7.77 | 2.146 | 7.13 | 56 | 1.98 | 70.8 | 0.279 | 0.025 | 38.87 | 9217 | 8.39 | 57 |  | 180.33 | 3.34 | 6.83 | -3.852 | 0.21 | 101
8/19/2025 10:30 | 6 | 19 | 2.75 | 7.93 | 2.276 | 7.14 | 56 | 1.98 | 70.8 | 0.279 | 0.025 | 38.87 | 9217 | 8.39 | 57 |  | 180.66 | 3.28 | 6.82 | -3.852 | 0.21 | 101
8/19/2025 10:45 | 4 | 19 | 2.75 | 7.952 | 2.244 | 7.14 | 56 | 1.98 | 70.8 | 0.279 | 0.025 | 38.87 | 9217 | 8.4 | 57 |  | 180.76 | 3.27 | 6.81 | -3.852 | 0.21 | 101
8/19/2025 11:00 | 7 | 19 | 2.75 | 7.888 | 2.212 | 7.13 | 56 | 1.98 | 70.8 | 0.279 | 0.025 | 38.87 | 9217 | 8.4 | 57 |  | 180.3 | 3.29 | 6.81 | -3.852 | 0.22 | 101
8/19/2025 11:15 | 7 | 19 | 2.75 | 7.854 | 2.232 | 7.14 | 56 | 1.98 | 70.8 | 0.279 | 0.025 | 38.87 | 9217 | 8.4 | 57 |  | 181.04 | 3.32 | 6.8 | -3.852 | 0.21 | 101
8/19/2025 11:30 | 4 | 19 | 2.75 | 7.64 | 2.137 | 7.14 | 56 | 1.98 | 70.8 | 0.279 | 0.025 | 38.87 | 9217 | 8.4 | 57 |  | 180.6 | 3.4 | 6.8 | -3.852 | 0.22 | 101
8/19/2025 11:45 | 9 | 19 | 2.75 | 7.658 | 2.053 | 7.14 | 56 | 1.98 | 70.8 | 0.279 | 0.025 | 38.87 | 9217 | 8.4 | 57 |  | 0 | 0 | 6.79 | -3.852 | 0.21 | 101
8/19/2025 12:00 | 7 | 19 | 2.75 | 8.045 | 2.373 | 7.19 | 56 | 1.98 | 70.8 | 0.159 | 0.025 | 38.87 | 9217 | 8.4 | 57 |  | 0 | 0 | 6.78 | -3.588 | 0.21 | 101
8/19/2025 12:15 | 6 | 19 | 2.75 | 8.135 | 2.334 | 7.2 | 56 | 1.98 | 70.8 | 0.159 | 0.026 | 39.17 | 9322 | 8.39 | 57 |  | 0 | 0 | 6.77 | -3.588 | 0.21 | 101
8/19/2025 12:30 | 8 | 19 | 2.75 | 8.129 | 2.344 | 7.21 | 56 | 1.98 | 70.8 | 0.159 | 0.026 | 39.17 | 9322 | 8.39 | 57 |  | 0 | 0 | 6.76 | -3.588 | 0.22 | 101
8/19/2025 12:45 | 8 | 19 | 2.75 | 7.701 | 2.251 | 7.22 | 56 | 1.98 | 70.8 | 0.159 | 0.027 | 39.17 | 9322 | 8.4 | 57 |  | 0 | 0 | 6.75 | -3.588 | 0.22 | 101
8/19/2025 13:00 | 8 | 19 | 2.75 | 7.712 | 2.392 | 7.22 | 56 | 1.98 | 70.8 | 0.159 | 0.027 | 39.17 | 9322 | 8.4 | 57 |  | 0 | 0 | 6.75 | -3.588 | 0.21 | 101
8/19/2025 13:15 | 8 | 19 | 2.75 | 8.001 | 2.468 | 7.21 | 56 | 1.98 | 70.8 | 0.159 | 0.027 | 39.17 | 9322 | 8.39 | 57 |  | 0 | 0 | 6.74 | -3.588 | 0.22 | 101
8/19/2025 13:30 | 5 | 19 | 2.75 | 7.952 | 2.437 | 7.22 | 56 | 1.98 | 70.8 | 0.159 | 0.027 | 39.17 | 9322 | 8.38 | 57 |  | 0 | 0 | 6.74 | -3.588 | 0.2 | 101
8/19/2025 13:45 | 7 | 19 | 2.75 | 8.022 | 2.607 | 7.22 | 56 | 1.98 | 70.8 | 0.159 | 0.026 | 39.17 | 9322 | 8.38 | 57 |  | 0 | 0 | 6.73 | -3.588 | 0.21 | 101
8/19/2025 14:00 | 7 | 19 | 2.75 | 7.951 | 3.063 | 7.19 | 56 | 1.98 | 71 | 0.159 | 0.026 | 39.17 | 9322 | 8.4 | 57 |  | 0 | 0 | 6.72 | -3.588 | 0.2 | 101
8/19/2025 14:15 | 6 | 19 | 2.75 | 8.036 | 2.881 | 7.21 | 56 | 1.98 | 71 | 0.159 | 0.026 | 39.17 | 9322 | 8.42 | 57 |  | 0 | 0 | 6.72 | -3.588 | 0.2 | 101
8/19/2025 14:30 | 6 | 19 | 2.75 | 8.036 | 3.119 | 7.23 | 56 | 1.98 | 71 | 0.159 | 0.026 | 39.17 | 9322 | 8.43 | 57 |  | 0 | 0 | 6.71 | -3.588 | 0.19 | 101
8/19/2025 14:45 | 7 | 19 | 2.75 | 8.018 | 3.799 | 7.21 | 56 | 1.98 | 71 | 0.159 | 0.026 | 39.17 | 9322 | 8.43 | 57 |  | 0 | 0 | 6.71 | -3.588 | 0.19 | 101
8/19/2025 15:00 | 3 | 19 | 2.75 | 8.031 | 4.577 | 7.21 | 56 | 1.98 | 71 | 0.159 | 0.026 | 39.17 | 9322 | 8.42 | 57 |  | 0 | 0 | 6.71 | -3.588 | 0.19 | 101
8/19/2025 15:15 | 3 | 19 | 2.75 | 8.015 | 4.351 | 7.21 | 56 | 1.98 | 71 | 0.159 | 0.026 | 39.17 | 9322 | 8.42 | 57 |  | 0 | 0 | 6.7 | -3.588 | 0.2 | 101
8/19/2025 15:30 | 5 | 19 | 2.75 | 7.457 | 3.95 | 7.22 | 56 | 1.98 | 71 | 0.159 | 0.026 | 39.17 | 9322 | 8.42 | 57 |  | 0 | 0 | 6.7 | -3.588 | 0.2 | 101
8/19/2025 15:45 | 4 | 19 | 2.75 | 7.409 | 4.003 | 7.21 | 56 | 1.98 | 71 | 0.159 | 0.026 | 39.17 | 9322 | 8.41 | 57 |  | 171.22 | 3.33 | 6.7 | -3.588 | 0.19 | 101
8/19/2025 16:00 | 6 | 19 | 2.75 | 7.655 | 3.236 | 7.15 | 56 | 1.98 | 71 | 0.135 | 0.026 | 39.17 | 9322 | 8.41 | 57 |  | 180.85 | 3.4 | 6.69 | -3.588 | 0.2 | 101
8/19/2025 16:15 | 7 | 19 | 2.75 | 7.692 | 2.952 | 7.15 | 56 | 1.98 | 71 | 0.135 | 0.025 | 39.17 | 9322 | 8.41 | 57 |  | 181.36 | 3.4 | 6.69 | -3.588 | 0.19 | 101
8/19/2025 16:30 | 7 | 19 | 2.75 | 7.893 | 2.702 | 7.16 | 56 | 1.98 | 71 | 0.135 | 0.025 | 39.17 | 9322 | 8.42 | 57 |  | 181.17 | 3.31 | 6.69 | -3.588 | 0.21 | 101
8/19/2025 16:45 | 6 | 19 | 2.75 | 7.962 | 2.658 | 7.16 | 56 | 1.98 | 71 | 0.135 | 0.025 | 39.17 | 9322 | 8.42 | 57 |  | 181.68 | 3.29 | 6.69 | -3.588 | 0.18 | 101
8/19/2025 17:00 | 7 | 19 | 2.75 | 7.833 | 3.396 | 7.14 | 56 | 1.98 | 71 | 0.135 | 0.025 | 39.17 | 9322 | 8.41 | 57 |  | 181.53 | 3.34 | 6.69 | -3.588 | 0.18 | 101
8/19/2025 17:15 | 8 | 19 | 2.75 | 7.447 | 3.094 | 7.14 | 56 | 1.98 | 71 | 0.135 | 0.025 | 39.17 | 9322 | 8.42 | 57 |  | 181.03 | 3.5 | 6.68 | -3.588 | 0.19 | 101
8/19/2025 17:30 | 8 | 19 | 2.75 | 7.492 | 3.15 | 7.13 | 56 | 1.98 | 71 | 0.135 | 0.025 | 39.17 | 9322 | 8.42 | 57 |  | 181.05 | 3.48 | 6.67 | -3.588 | 0.19 | 101
8/19/2025 17:45 | 6 | 19 | 2.75 | 7.61 | 3.039 | 7.13 | 56 | 1.98 | 71 | 0.135 | 0.025 | 39.17 | 9322 | 8.43 | 57 |  | 180.91 | 3.42 | 6.67 | -3.588 | 0.18 | 101
8/19/2025 18:00 | 5 | 19 | 2.75 | 7.638 | 2.928 | 7.14 | 56 | 1.98 | 71.2 | 0.135 | 0.025 | 39.17 | 9322 | 8.42 | 57 |  | 181.26 | 3.42 | 6.67 | -3.588 | 0.18 | 101
8/19/2025 18:15 | 8 | 19 | 2.75 | 7.808 | 2.81 | 7.15 | 56 | 1.98 | 71.2 | 0.135 | 0.025 | 39.45 | 9407 | 8.43 | 57 |  | 180.91 | 3.34 | 6.66 | -3.588 | 0.18 | 101
8/19/2025 18:30 | 1 | 19 | 2.75 | 7.812 | 2.895 | 7.15 | 56 | 1.98 | 71.2 | 0.135 | 0.026 | 39.45 | 9407 | 8.44 | 57 |  | 181.33 | 3.34 | 6.66 | -3.588 | 0.19 | 101
8/19/2025 18:45 | 6 | 19 | 2.75 | 7.831 | 3.32 | 7.13 | 56 | 1.98 | 71.2 | 0.135 | 0.027 | 39.45 | 9407 | 8.45 | 57 |  | 181 | 3.33 | 6.66 | -3.588 | 0.2 | 101
8/19/2025 19:00 | 6 | 19 | 2.75 | 7.944 | 3.081 | 7.13 | 56 | 1.98 | 71.2 | 0.135 | 0.027 | 39.45 | 9407 | 8.46 | 57 |  | 181.14 | 3.28 | 6.66 | -3.588 | 0.19 | 101
8/19/2025 19:15 | 8 | 19 | 2.75 | 7.99 | 2.734 | 7.14 | 56 | 1.98 | 71.2 | 0.135 | 0.027 | 39.45 | 9407 | 8.45 | 57 |  | 181 | 3.26 | 6.66 | -3.588 | 0.2 | 101
8/19/2025 19:30 | 8 | 19 | 2.75 | 8.215 | 2.629 | 7.15 | 56 | 1.98 | 71.2 | 0.135 | 0.027 | 39.45 | 9407 | 8.43 | 57 |  | 180.97 | 3.17 | 6.65 | -3.588 | 0.19 | 101
8/19/2025 19:45 | 9 | 19 | 2.75 | 8.269 | 2.729 | 7.14 | 56 | 1.98 | 71.2 | 0.135 | 0.027 | 39.45 | 9407 | 8.41 | 57 |  | 181.3 | 3.16 | 6.65 | -3.588 | 0.18 | 101
8/19/2025 20:00 | 9 | 19 | 2.75 | 8.299 | 2.814 | 7.13 | 56 | 1.98 | 71.2 | 0.196 | 0.027 | 39.45 | 9407 | 8.43 | 57 |  | 180.69 | 3.14 | 6.65 | -3.588 | 0.19 | 101
8/19/2025 20:15 | 5 | 19 | 2.75 | 8.21 | 2.726 | 7.13 | 56 | 1.98 | 71.2 | 0.196 | 0.027 | 39.45 | 9407 | 8.45 | 57 |  | 181.26 | 3.18 | 6.64 | -3.588 | 0.19 | 101
8/19/2025 20:30 | 6 | 19 | 2.75 | 8.313 | 2.675 | 7.13 | 56 | 1.98 | 71.2 | 0.196 | 0.027 | 39.45 | 9407 | 8.45 | 57 |  | 180.72 | 3.13 | 6.64 | -3.588 | 0.18 | 101
8/19/2025 20:45 | 5 | 19 | 2.75 | 8.261 | 2.744 | 7.12 | 56 | 1.98 | 71.2 | 0.196 | 0.027 | 39.45 | 9407 | 8.45 | 57 |  | 181.35 | 3.16 | 6.63 | -3.588 | 0.18 | 101
8/19/2025 21:00 | 5 | 19 | 2.75 | 8.258 | 2.746 | 7.11 | 56 | 1.98 | 71.2 | 0.196 | 0.027 | 39.45 | 9407 | 8.44 | 57 |  | 180.36 | 3.15 | 6.62 | -3.588 | 0.19 | 101
8/19/2025 21:15 | 2 | 19 | 2.75 | 8.224 | 2.692 | 7.12 | 56 | 1.98 | 71.2 | 0.196 | 0.027 | 39.45 | 9407 | 8.44 | 57 |  | 180.24 | 3.16 | 6.61 | -3.588 | 0.18 | 101
8/19/2025 21:30 | 8 | 19 | 2.75 | 8.213 | 2.627 | 7.12 | 56 | 1.98 | 71.2 | 0.196 | 0.027 | 39.45 | 9407 | 8.42 | 57 |  | 180.51 | 3.16 | 6.62 | -3.588 | 0.2 | 101
8/19/2025 21:45 | 6 | 19 | 2.75 | 8.287 | 2.651 | 7.12 | 56 | 1.98 | 71.2 | 0.196 | 0.027 | 39.45 | 9407 | 8.42 | 57 |  | 180.83 | 3.14 | 6.62 | -3.588 | 0.18 | 101
8/19/2025 22:00 | 6 | 19 | 2.75 | 7.735 | 2.691 | 7.11 | 55 | 1.98 | 71.4 | 0.196 | 0.027 | 39.45 | 9407 | 8.4 | 57 |  | 179.85 | 3.35 | 6.62 | -3.588 | 0.18 | 101
8/19/2025 22:15 | 6 | 19 | 2.75 | 7.607 | 2.728 | 7.11 | 55 | 1.98 | 71.4 | 0.196 | 0.027 | 39.45 | 9407 | 8.4 | 57 |  | 179.68 | 3.4 | 6.64 | -3.588 | 0.19 | 101
8/19/2025 22:30 | 7 | 19 | 2.75 | 8.027 | 2.69 | 7.11 | 55 | 1.98 | 71.4 | 0.196 | 0.027 | 39.45 | 9407 | 8.39 | 57 |  | 180.16 | 3.23 | 6.65 | -3.588 | 0.2 | 101
8/19/2025 22:45 | 7 | 19 | 2.75 | 8.007 | 2.585 | 7.12 | 55 | 1.98 | 71.4 | 0.196 | 0.026 | 39.45 | 9407 | 8.38 | 57 |  | 179.91 | 3.24 | 6.65 | -3.588 | 0.28 | 101
8/19/2025 23:00 | 7 | 19 | 2.75 | 7.961 | 2.444 | 7.12 | 55 | 1.98 | 71.4 | 0.196 | 0.026 | 39.45 | 9407 | 8.37 | 57 |  | 0 | 0 | 6.64 | -3.588 | 0.21 | 101
8/19/2025 23:15 | 7 | 19 | 2.75 | 7.975 | 2.811 | 7.15 | 55 | 1.98 | 71.4 | 0.196 | 0.026 | 39.45 | 9407 | 8.37 | 57 |  | 0 | 0 | 6.65 | -3.588 | 0.19 | 101
8/19/2025 23:30 | 6 | 19 | 2.75 | 8.033 | 2.799 | 7.15 | 55 | 1.98 | 71.4 | 0.196 | 0.026 | 39.45 | 9407 | 8.36 | 57 |  | 0 | 0 | 6.65 | -3.588 | 0.23 | 101
8/19/2025 23:45 | 1 | 19 | 2.75 | 8.019 | 2.852 | 7.16 | 55 | 1.98 | 71.4 | 0.196 | 0.026 | 39.45 | 9407 | 8.35 | 57 |  | 0 | 0 | 6.66 | -3.588 | 0.23 | 101
8/20/2025 00:00 | 3 | 19 | 2.75 | 8.027 | 2.987 | 7.15 | 55 | 1.98 | 71.4 | 0.285 | 0.026 | 39.45 | 9407 | 8.35 | 57 | 1.51 | 0 | 0 | 6.66 | -3.588 | 0.19 | 101
8/20/2025 00:15 | 4 | 19 | 2.75 | 8.036 | 3.053 | 7.15 | 55 | 1.98 | 71.4 | 0.285 | 0.026 | 39.45 | 9407 | 8.35 | 57 | 1.51 | 0 | 0 | 6.67 | -3.588 | 0.19 | 101
8/20/2025 00:30 | 3 | 19 | 2.75 | 7.999 | 3.121 | 7.15 | 55 | 1.98 | 71.4 | 0.285 | 0.026 | 39.45 | 9407 | 8.36 | 57 | 1.51 | 0 | 0 | 6.67 | -3.588 | 0.18 | 101
8/20/2025 00:45 | 1 | 19 | 2.75 | 8.012 | 3.108 | 7.15 | 55 | 1.98 | 71.4 | 0.285 | 0.026 | 39.45 | 9407 | 8.36 | 57 | 1.51 | 0 | 0 | 6.67 | -3.588 | 0.18 | 101
8/20/2025 01:00 | 0 | 19 | 2.75 | 7.918 | 3.18 | 7.15 | 55 | 1.98 | 71.4 | 0.285 | 0.026 | 39.45 | 9407 | 8.35 | 57 | 1.51 | 0 | 0 | 6.67 | -3.588 | 0.2 | 101
8/20/2025 01:15 | 2 | 19 | 2.75 | 7.923 | 3.169 | 7.15 | 55 | 1.98 | 71.4 | 0.285 | 0.026 | 39.45 | 9407 | 8.35 | 57 | 1.51 | 0 | 0 | 6.66 | -3.588 | 0.29 | 101
8/20/2025 01:30 | 3 | 19 | 2.75 | 8.09 | 3.264 | 7.14 | 55 | 1.98 | 71.4 | 0.285 | 0.026 | 39.45 | 9407 | 8.35 | 57 | 1.51 | 0 | 0 | 6.66 | -3.588 | 0.17 | 101
8/20/2025 01:45 | 0 | 19 | 2.75 | 8.14 | 3.33 | 7.14 | 55 | 1.98 | 71.4 | 0.285 | 0.026 | 39.45 | 9407 | 8.34 | 57 | 1.51 | 0 | 0 | 6.66 | -3.588 | 0.2 | 101
8/20/2025 02:00 | 2 | 19 | 2.75 | 8.147 | 3.29 | 7.14 | 55 | 1.98 | 71.2 | 0.285 | 0.026 | 39.45 | 9407 | 8.34 | 57 | 1.51 | 0 | 0 | 6.66 | -3.588 | 0.19 | 101
8/20/2025 02:15 | -1 | 19 | 2.75 | 8.137 | 3.22 | 7.14 | 55 | 1.98 | 71.2 | 0.285 | 0.026 | 39.45 | 9407 | 8.33 | 57 | 1.51 | 0 | 0 | 6.66 | -3.588 | 0.19 | 101
8/20/2025 02:30 | 2 | 19 | 2.75 | 7.55 | 3.224 | 7.13 | 55 | 1.98 | 71.2 | 0.285 | 0.026 | 39.45 | 9407 | 8.33 | 57 | 1.51 | 0 | 0 | 6.65 | -3.588 | 0.19 | 101
8/20/2025 02:45 | -2 | 19 | 2.75 | 7.567 | 3.217 | 7.13 | 55 | 1.98 | 71.2 | 0.285 | 0.026 | 39.45 | 9407 | 8.32 | 57 | 1.51 | 0 | 0 | 6.65 | -3.588 | 0.2 | 101
8/20/2025 03:00 | -1 | 19 | 2.75 | 8.046 | 3.229 | 7.13 | 55 | 1.98 | 71.2 | 0.285 | 0.025 | 39.45 | 9407 | 8.31 | 57 | 1.51 | 0 | 0 | 6.66 | -3.588 | 0.18 | 101
8/20/2025 03:15 | -2 | 19 | 2.75 | 8.034 | 3.281 | 7.13 | 55 | 1.98 | 71.2 | 0.285 | 0.025 | 39.45 | 9407 | 8.31 | 57 | 1.51 | 0 | 0 | 6.66 | -3.588 | 0.18 | 101
8/20/2025 03:30 | -4 | 19 | 2.75 | 8.003 | 3.192 | 7.13 | 55 | 1.98 | 71.2 | 0.285 | 0.025 | 39.45 | 9407 | 8.31 | 57 | 1.51 | 0 | 0 | 6.66 | -3.588 | 0.19 | 101
8/20/2025 03:45 | -1 | 19 | 2.75 | 8.007 | 3.252 | 7.13 | 55 | 1.98 | 71.2 | 0.285 | 0.025 | 39.45 | 9407 | 8.3 | 57 | 1.51 | 0 | 0 | 6.67 | -3.588 | 0.19 | 101
8/20/2025 04:00 | -9 | 19 | 2.75 | 8.021 | 3.243 | 7.13 | 55 | 1.98 | 71.2 | 0.278 | 0.025 | 38.8 | 9199 | 8.3 | 57 | 1.51 | 0 | 0 | 6.67 | -3.588 | 0.21 | 101
8/20/2025 04:15 | 0 | 19 | 2.75 | 7.95 | 3.29 | 7.13 | 55 | 1.98 | 71.2 | 0.278 | 0.026 | 38.8 | 9199 | 8.3 | 57 | 1.51 | 0 | 0 | 6.68 | -3.588 | 0.21 | 101
8/20/2025 04:30 | -2 | 19 | 2.75 | 7.912 | 3.313 | 7.13 | 55 | 1.98 | 71.2 | 0.278 | 0.026 | 38.8 | 9199 | 8.29 | 57 | 1.51 | 0 | 0 | 6.68 | -3.588 | 0.21 | 101
8/20/2025 04:45 | 0 | 19 | 2.75 | 7.853 | 3.425 | 7.13 | 55 | 1.98 | 71.2 | 0.278 | 0.027 | 38.8 | 9199 | 8.29 | 57 | 1.51 | 0 | 0 | 6.68 | -3.588 | 0.21 | 101
8/20/2025 05:00 | -5 | 19 | 2.75 | 7.922 | 3.444 | 7.13 | 55 | 1.98 | 71.2 | 0.278 | 0.027 | 38.07 | 9125 | 8.29 | 57 | 1.51 | 0 | 0 | 6.68 | -3.588 | 0.21 | 101
8/20/2025 05:15 | -3 | 19 | 2.75 | 7.807 | 3.432 | 7.13 | 55 | 1.98 | 71.2 | 0.278 | 0.028 | 38.07 | 9125 | 8.28 | 57 | 1.51 | 0 | 0 | 6.67 | -3.588 | 0.2 | 101
8/20/2025 05:30 | -1 | 19 | 2.75 | 7.894 | 3.345 | 7.13 | 55 | 1.98 | 71.2 | 0.278 | 0.028 | 38.07 | 9125 | 8.3 | 57 | 1.51 | 0 | 0 | 6.67 | -3.588 | 0.31 | 101
8/20/2025 05:45 | -4 | 19 | 2.75 | 7.86 | 3.438 | 7.12 | 55 | 1.98 | 71.2 | 0.278 | 0.028 | 38.07 | 9125 | 8.34 | 57 | 1.51 | 0 | 0 | 6.67 | -3.588 | 0.19 | 101
8/20/2025 06:00 | -1 | 19 | 2.75 | 7.822 | 3.455 | 7.12 | 55 | 1.98 | 71 | 0.278 | 0.028 | 38.07 | 9125 | 8.36 | 57 | 1.51 | 0 | 0 | 6.67 | -3.588 | 0.19 | 101
8/20/2025 06:15 | 0 | 19 | 2.75 | 7.833 | 3.462 | 7.12 | 55 | 1.98 | 71 | 0.278 | 0.028 | 38.07 | 9125 | 8.35 | 57 | 1.51 | 0 | 0 | 6.67 | -3.588 | 0.19 | 101
8/20/2025 06:30 | -3 | 19 | 2.75 | 7.838 | 3.405 | 7.12 | 55 | 1.98 | 71 | 0.278 | 0.028 | 38.07 | 9125 | 8.37 | 57 | 1.51 | 0 | 0 | 6.68 | -3.588 | 0.2 | 101
8/20/2025 06:45 | -3 | 19 | 2.75 | 7.947 | 3.422 | 7.12 | 55 | 1.98 | 71 | 0.278 | 0.027 | 38.07 | 9125 | 8.39 | 57 | 1.51 | 0 | 0 | 6.68 | -3.588 | 0.19 | 101
8/20/2025 07:00 | 0 | 19 | 2.75 | 7.933 | 3.455 | 7.13 | 55 | 1.98 | 71 | 0.278 | 0.027 | 38.07 | 9125 | 8.38 | 57 | 1.51 | 0 | 0 | 6.68 | -3.588 | 0.18 | 101
8/20/2025 07:15 | 0 | 19 | 2.75 | 7.942 | 3.292 | 7.09 | 55 | 1.98 | 71 | 0.278 | 0.027 | 38.07 | 9125 | 8.37 | 57 | 1.51 | 179.27 | 3.25 | 6.68 | -3.588 | 0.21 | 101
8/20/2025 07:30 | -3 | 19 | 2.75 | 7.956 | 3.453 | 7.07 | 55 | 1.98 | 71 | 0.278 | 0.027 | 38.07 | 9125 | 7.77 | 57 | 1.51 | 179.01 | 3.24 | 6.69 | -3.588 | 0.22 | 101
8/20/2025 07:45 | -1 | 19 | 2.75 | 8.005 | 3.349 | 7.1 | 55 | 1.98 | 71 | 0.278 | 0.027 | 38.07 | 9125 | 8.28 | 57 | 1.51 | 179.21 | 3.22 | 6.69 | -3.588 | 0.17 | 101
8/20/2025 08:00 | 0 | 21 | 2.75 | 8.03 | 3.272 | 7.11 | 55 | 1.98 | 71 | 0.29 | 0.027 | 38.07 | 9125 | 8.28 | 57 | 1.51 | 0 | 0 | 6.7 | -3.588 | 0.21 | 101
8/20/2025 08:15 | -5 | 21 | 2.75 | 7.968 | 3.666 | 7.15 | 55 | 1.98 | 71 | 0.29 | 0.026 | 38.07 | 9125 | 8.27 | 57 | 1.51 | 0 | 0 | 6.71 | -3.588 | 0.2 | 101
8/20/2025 08:30 | 0 | 21 | 2.75 | 7.994 | 3.486 | 7.16 | 55 | 1.98 | 71 | 0.29 | 0.026 | 38.07 | 9125 | 8.26 | 57 | 1.51 | 0 | 0 | 6.71 | -3.588 | 0.2 | 101
8/20/2025 08:45 | 6 | 21 | 2.75 | 7.934 | 3.222 | 7.16 | 55 | 1.98 | 71 | 0.29 | 0.026 | 38.07 | 9125 | 8.25 | 57 | 1.51 | 0 | 0 | 6.71 | -3.588 | 0.21 | 101
8/20/2025 09:00 | 5 | 21 | 2.75 | 7.944 | 3.229 | 7.16 | 55 | 1.98 | 71 | 0.29 | 0.026 | 38.07 | 9125 | 8.25 | 57 | 1.51 | 0 | 0 | 6.71 | -3.588 | 0.19 | 101
8/20/2025 09:15 | 8 | 21 | 2.75 | 7.931 | 3.311 | 7.16 | 55 | 1.98 | 71 | 0.29 | 0.026 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.71 | -3.588 | 0.2 | 101
8/20/2025 09:30 | 7 | 17 | 2.75 | 7.959 | 3.312 | 7.16 | 55 | 1.98 | 71 | 0.29 | 0.026 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.71 | -3.588 | 0.19 | 101
8/20/2025 09:45 | 5 | 17 | 2.75 | 7.909 | 3.327 | 7.16 | 55 | 1.98 | 71 | 0.29 | 0.026 | 38.07 | 9125 | 8.23 | 57 | 1.51 | 0 | 0 | 6.71 | -3.588 | 0.19 | 101
8/20/2025 10:00 | -9 | 17 | 2.75 | 7.871 | 3.404 | 7.16 | 56 | 1.98 | 71 | 0.29 | 0.026 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.71 | -3.588 | 0.18 | 101
8/20/2025 10:15 | -7 | 17 | 2.75 | 7.942 | 3.165 | 7.14 | 56 | 1.98 | 71 | 0.29 | 0.026 | 38.07 | 9125 | 8.23 | 57 | 1.51 | 0 | 0 | 6.7 | -3.588 | 0.17 | 101
8/20/2025 10:30 | -13 | 17 | 2.75 | 7.914 | 3.221 | 7.16 | 56 | 1.98 | 71 | 0.29 | 0.026 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.7 | -3.588 | 0.17 | 100
8/20/2025 10:45 | -8 | 17 | 2.75 | 7.933 | 3.027 | 7.17 | 56 | 1.98 | 71 | 0.29 | 0.026 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 7.07 | -3.588 | 0.18 | 101
8/20/2025 11:00 | -12 | 17 | 2.75 | 7.869 | 2.877 | 7.18 | 56 | 1.98 | 71 | 0.29 | 0.026 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.82 | -3.588 | 0.25 | 101
8/20/2025 11:15 | -4 | 17 | 2.75 | 7.912 | 2.718 | 7.18 | 56 | 1.98 | 71 | 0.29 | 0.026 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.82 | -3.588 | 0.23 | 101
8/20/2025 11:30 | 0 | 17 | 2.75 | 7.945 | 2.634 | 7.19 | 56 | 1.98 | 71 | 0.29 | 0.025 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.89 | -3.588 | 0.25 | 101
8/20/2025 11:45 | 0 | 17 | 2.75 | 7.865 | 2.867 | 7.18 | 56 | 1.98 | 71 | 0.29 | 0.025 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.92 | -3.588 | 0.23 | 101
8/20/2025 12:00 | -4 | 19 | 2.75 | 7.878 | 2.91 | 7.18 | 56 | 1.98 | 71 | 0.158 | 0.025 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.88 | -3.787 | 0.24 | 101
8/20/2025 12:15 | 5 | 19 | 2.75 | 7.868 | 2.867 | 7.18 | 56 | 1.98 | 71 | 0.158 | 0.025 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.87 | -3.787 | 0.24 | 101
8/20/2025 12:30 | 7 | 19 | 2.75 | 7.958 | 2.829 | 7.19 | 56 | 1.98 | 71 | 0.158 | 0.025 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.87 | -3.787 | 0.24 | 101
8/20/2025 12:45 | 7 | 19 | 2.75 | 7.891 | 2.734 | 7.19 | 56 | 1.98 | 71 | 0.158 | 0.025 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.87 | -3.787 | 0.23 | 101
8/20/2025 13:00 | 7 | 19 | 2.75 | 7.912 | 2.75 | 7.19 | 56 | 1.98 | 71 | 0.158 | 0.025 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.86 | -3.787 | 0.23 | 101
8/20/2025 13:15 | 9 | 19 | 2.75 | 7.856 | 2.726 | 7.19 | 56 | 1.98 | 71 | 0.158 | 0.025 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.86 | -3.787 | 0.24 | 101
8/20/2025 13:30 | 10 | 19 | 2.75 | 7.935 | 3.022 | 7.17 | 56 | 1.98 | 71 | 0.158 | 0.025 | 38.07 | 9125 | 8.24 | 57 | 1.51 | 0 | 0 | 6.84 | -3.787 | 0.23 | 101
8/20/2025 13:45 | 6 | 19 | 2.75 | 7.993 | 3.047 | 7.17 | 56 | 1.98 | 71 | 0.158 | 0.025 | 38.07 | 9125 | 8.23 | 57 | 1.51 | 0 | 0 | 6.84 | -3.787 | 0.23 | 101
8/20/2025 14:00 | -5 | 19 | 2.75 | 8.02 | 2.986 | 7.18 | 56 | 1.98 | 71.2 | 0.158 | 0.026 | 38.07 | 9125 | 8.23 | 55 | 1.51 | 0 | 0 | 6.84 | -3.787 | 0.23 | 101
8/20/2025 14:15 | 7 | 19 | 2.75 | 8.14 | 3.137 | 7.17 | 56 | 1.98 | 71.2 | 0.158 | 0.025 | 38.07 | 9125 | 8.22 | 55 | 1.51 | 0 | 0 | 6.83 | -3.787 | 0.23 | 101
8/20/2025 14:30 | 8 | 19 | 2.75 | 8.043 | 3.073 | 7.17 | 56 | 1.98 | 71.2 | 0.158 | 0.025 | 38.07 | 9125 | 8.22 | 55 | 1.51 | 0 | 0 | 6.83 | -3.787 | 0.23 | 101
8/20/2025 14:45 | 8 | 19 | 2.75 | 8.044 | 3.108 | 7.19 | 56 | 1.98 | 71.2 | 0.158 | 0.025 | 38.07 | 9125 | 8.22 | 55 | 1.51 | 0 | 0 | 6.84 | -3.787 | 0.23 | 101
8/20/2025 15:00 | 9 | 19 | 2.75 | 7.971 | 2.967 | 7.2 | 56 | 1.98 | 71.2 | 0.158 | 0.025 | 38.07 | 9125 | 8.21 | 55 | 1.51 | 0 | 0 | 6.85 | -3.787 | 0.24 | 101
8/20/2025 15:15 | 8 | 19 | 2.75 | 7.764 | 3.178 | 7.17 | 56 | 1.98 | 71.2 | 0.158 | 0.025 | 38.07 | 9125 | 8.21 | 55 | 1.51 | 0 | 0 | 6.83 | -3.787 | 0.23 | 101
8/20/2025 15:30 | 9 | 19 | 2.75 | 7.869 | 3.396 | 7.16 | 56 | 1.98 | 71.2 | 0.158 | 0.025 | 38.07 | 9125 | 8.21 | 55 | 1.51 | 0 | 0 | 6.82 | -3.787 | 0.23 | 101
8/20/2025 15:45 | 8 | 19 | 2.75 | 7.912 | 3.585 | 7.16 | 56 | 1.98 | 71.2 | 0.158 | 0.024 | 38.07 | 9125 | 8.21 | 55 | 1.51 | 0 | 0 | 6.82 | -3.787 | 0.23 | 101
8/20/2025 16:00 | 6 | 19 | 2.75 | 7.881 | 3.61 | 7.18 | 56 | 1.98 | 71.2 | 0.144 | 0.024 | 38.07 | 9125 | 8.21 | 55 | 1.51 | 0 | 0 | 6.84 | -3.787 | 0.24 | 101
8/20/2025 16:15 | 8 | 19 | 2.75 | 7.913 | 4.076 | 7.17 | 56 | 1.98 | 71.2 | 0.144 | 0.024 | 38.07 | 9125 | 8.2 | 55 | 1.51 | 0 | 0 | 6.82 | -3.787 | 0.23 | 101
8/20/2025 16:30 | 6 | 19 | 2.75 | 7.962 | 3.595 | 7.18 | 56 | 1.98 | 71.2 | 0.144 | 0.024 | 38.07 | 9125 | 8.2 | 55 | 1.51 | 0 | 0 | 6.83 | -3.787 | 0.24 | 101
8/20/2025 16:45 | 10 | 19 | 2.75 | 7.86 | 3.359 | 7.2 | 56 | 1.98 | 71.2 | 0.144 | 0.024 | 38.07 | 9125 | 8.2 | 55 | 1.51 | 0 | 0 | 6.85 | -3.787 | 0.24 | 101
8/20/2025 17:00 | 12 | 19 | 2.75 | 7.89 | 3.31 | 7.19 | 56 | 1.98 | 71.2 | 0.144 | 0.024 | 38.07 | 9125 | 8.2 | 55 | 1.51 | 0 | 0 | 6.85 | -3.787 | 0.24 | 101
8/20/2025 17:15 | 9 | 19 | 2.75 | 7.856 | 3.272 | 7.19 | 56 | 1.98 | 71.2 | 0.144 | 0.024 | 38.07 | 9125 | 8.21 | 55 | 1.51 | 0 | 0 | 6.84 | -3.787 | 0.25 | 101
8/20/2025 17:30 | 11 | 19 | 2.75 | 7.873 | 3.286 | 7.19 | 56 | 1.98 | 71.2 | 0.144 | 0.024 | 38.07 | 9125 | 8.22 | 55 | 1.51 | 0 | 0 | 6.84 | -3.787 | 0.23 | 101
8/20/2025 17:45 | 9 | 19 | 2.75 | 7.902 | 3.356 | 7.19 | 56 | 1.98 | 71.2 | 0.144 | 0.024 | 38.07 | 9125 | 8.22 | 55 | 1.51 | 0 | 0 | 6.83 | -3.787 | 0.23 | 101
8/20/2025 18:00 | 12 | 19 | 2.75 | 8.179 | 3.389 | 7.2 | 56 | 1.98 | 71.4 | 0.144 | 0.025 | 37.66 | 9110 | 8.24 | 55 | 1.51 | 0 | 0 | 6.84 | -3.787 | 0.23 | 101
8/20/2025 18:15 | 12 | 19 | 2.75 | 8.164 | 3.306 | 7.2 | 56 | 1.98 | 71.4 | 0.144 | 0.026 | 37.66 | 9110 | 8.25 | 55 | 1.51 | 0 | 0 | 6.84 | -3.787 | 0.23 | 101
8/20/2025 18:30 | 11 | 19 | 2.75 | 7.457 | 3.077 | 7.21 | 56 | 1.98 | 71.4 | 0.144 | 0.027 | 37.66 | 9110 | 8.26 | 55 | 1.51 | 0 | 0 | 6.86 | -3.787 | 0.23 | 101
8/20/2025 18:45 | 14 | 19 | 2.75 | 7.454 | 3.039 | 7.21 | 56 | 1.98 | 71.4 | 0.144 | 0.027 | 37.66 | 9110 | 8.27 | 55 | 1.51 | 0 | 0 | 6.86 | -3.787 | 0.22 | 100
8/20/2025 19:00 | 9 | 19 | 2.75 | 7.822 | 3.219 | 7.19 | 56 | 1.98 | 71.4 | 0.144 | 0.027 | 37.66 | 9110 | 8.27 | 55 | 1.51 | 0 | 0 | 6.85 | -3.787 | 0.23 | 101
8/20/2025 19:15 | 12 | 19 | 2.75 | 7.789 | 3.022 | 7.16 | 56 | 1.98 | 71.4 | 0.144 | 0.027 | 37.66 | 9110 | 8.26 | 55 | 1.51 | 177.29 | 3.28 | 6.83 | -3.787 | 0.24 | 101
8/20/2025 19:30 | 8 | 19 | 2.75 | 7.793 | 3.012 | 7.11 | 56 | 1.98 | 71.4 | 0.144 | 0.026 | 37.66 | 9110 | 8.27 | 55 | 1.51 | 177.69 | 3.28 | 6.81 | -3.787 | 0.23 | 101
8/20/2025 19:45 | 8 | 19 | 2.75 | 7.855 | 2.847 | 7.11 | 56 | 1.98 | 71.4 | 0.144 | 0.026 | 37.66 | 9110 | 8.31 | 55 | 1.51 | 177.42 | 3.25 | 6.8 | -3.787 | 0.23 | 101
8/20/2025 20:00 | 10 | 19 | 2.75 | 7.818 | 2.885 | 7.1 | 56 | 1.98 | 71.4 | 0.175 | 0.026 | 37.66 | 9110 | 8.35 | 55 | 1.51 | 177.08 | 3.26 | 6.8 | -3.787 | 0.24 | 101
8/20/2025 20:15 | 9 | 19 | 2.75 | 7.999 | 2.86 | 7.1 | 56 | 1.98 | 71.4 | 0.175 | 0.026 | 37.66 | 9110 | 8.37 | 55 | 1.51 | 177.08 | 3.19 | 6.8 | -3.787 | 0.22 | 101
8/20/2025 20:30 | 7 | 19 | 2.75 | 7.948 | 2.736 | 7.1 | 56 | 1.98 | 71.4 | 0.175 | 0.026 | 37.66 | 9110 | 8.38 | 55 | 1.51 | 177.41 | 3.21 | 6.8 | -3.787 | 0.23 | 101
8/20/2025 20:45 | 11 | 19 | 2.75 | 7.928 | 2.6 | 7.11 | 56 | 1.98 | 71.4 | 0.175 | 0.026 | 37.66 | 9110 | 8.38 | 55 | 1.51 | 177.7 | 3.23 | 6.81 | -3.787 | 0.23 | 101
8/20/2025 21:00 | 8 | 19 | 2.75 | 7.993 | 2.468 | 7.12 | 56 | 1.98 | 71.4 | 0.175 | 0.026 | 37.66 | 9110 | 8.37 | 55 | 1.51 | 176.44 | 3.18 | 6.81 | -3.787 | 0.23 | 101
8/20/2025 21:15 | 9 | 19 | 2.75 | 7.939 | 2.304 | 7.12 | 56 | 1.98 | 71.4 | 0.175 | 0.026 | 37.66 | 9110 | 8.37 | 55 | 1.51 | 176.53 | 3.2 | 6.82 | -3.787 | 0.23 | 101
8/20/2025 21:30 | 11 | 19 | 2.75 | 7.951 | 2.159 | 7.14 | 56 | 1.98 | 71.4 | 0.175 | 0.026 | 37.66 | 9110 | 8.35 | 55 | 1.51 | 176.88 | 3.2 | 6.84 | -3.787 | 0.23 | 101
8/20/2025 21:45 | 10 | 19 | 2.75 | 7.809 | 1.989 | 7.14 | 56 | 1.98 | 71.4 | 0.175 | 0.026 | 37.24 | 9096 | 8.35 | 55 | 1.51 | 177.13 | 3.27 | 6.85 | -3.787 | 0.22 | 101
8/20/2025 22:00 | 13 | 19 | 2.75 | 8.137 | 2.114 | 7.13 | 56 | 1.98 | 71.4 | 0.175 | 0.028 | 37.24 | 9096 | 8.35 | 55 | 1.51 | 0 | 0 | 6.84 | -3.787 | 0.22 | 101
8/20/2025 22:15 | 7 | 19 | 2.75 | 8.331 | 2.867 | 7.14 | 56 | 1.98 | 71.4 | 0.175 | 0.028 | 37.24 | 9096 | 8.34 | 55 | 1.51 | 0 | 0 | 6.81 | -3.787 | 0.21 | 101
8/20/2025 22:30 | 8 | 19 | 2.75 | 8.336 | 3.093 | 7.13 | 56 | 1.98 | 71.4 | 0.175 | 0.028 | 37.24 | 9096 | 8.34 | 55 | 1.51 | 0 | 0 | 6.8 | -3.787 | 0.2 | 101
8/20/2025 22:45 | 4 | 19 | 2.75 | 8.312 | 3.131 | 7.13 | 56 | 1.98 | 71.4 | 0.175 | 0.028 | 37.24 | 9096 | 8.34 | 55 | 1.51 | 0 | 0 | 6.8 | -3.787 | 0.22 | 101
8/20/2025 23:00 | 7 | 19 | 2.75 | 7.81 | 2.977 | 7.16 | 56 | 1.98 | 71.4 | 0.175 | 0.027 | 37.24 | 9096 | 8.33 | 55 | 1.51 | 0 | 0 | 6.83 | -3.787 | 0.21 | 101
8/20/2025 23:15 | 7 | 19 | 2.75 | 7.73 | 2.918 | 7.17 | 56 | 1.98 | 71.4 | 0.175 | 0.027 | 37.24 | 9096 | 8.35 | 55 | 1.51 | 0 | 0 | 6.84 | -3.787 | 0.23 | 101
8/20/2025 23:30 | 3 | 19 | 2.75 | 8.225 | 2.698 | 7.19 | 56 | 1.98 | 71.4 | 0.175 | 0.027 | 37.24 | 9096 | 8.38 | 55 | 1.51 | 0 | 0 | 6.85 | -3.787 | 0.24 | 101
8/20/2025 23:45 | 4 | 19 | 2.75 | 8.266 | 3.007 | 7.18 | 56 | 1.98 | 71.4 | 0.175 | 0.027 | 37.24 | 9096 | 8.39 | 55 | 1.51 | 0 | 0 | 6.84 | -3.787 | 0.25 | 101
8/21/2025 00:00 | 5 | 19 | 2.75 | 8.23 | 2.921 | 7.17 | 56 | 1.99 | 71.4 | 0.257 | 0.027 | 37.24 | 9096 | 8.38 | 55 |  | 0 | 0 | 6.83 | -3.787 | 0.24 | 101
8/21/2025 00:15 | 8 | 19 | 2.75 | 8.303 | 3.009 | 7.17 | 56 | 1.99 | 71.4 | 0.257 | 0.027 | 37.24 | 9096 | 8.36 | 55 |  | 0 | 0 | 6.82 | -3.787 | 0.24 | 101
8/21/2025 00:30 | 5 | 19 | 2.75 | 8.285 | 2.859 | 7.16 | 56 | 1.99 | 71.4 | 0.257 | 0.027 | 37.24 | 9096 | 8.35 | 55 |  | 0 | 0 | 6.81 | -3.787 | 0.27 | 101
8/21/2025 00:45 | 5 | 19 | 2.75 | 7.645 | 2.828 | 7.16 | 56 | 1.99 | 71.4 | 0.257 | 0.027 | 37.24 | 9096 | 8.33 | 55 |  | 0 | 0 | 6.81 | -3.787 | 0.23 | 101
8/21/2025 01:00 | 8 | 19 | 2.75 | 7.666 | 2.871 | 7.14 | 56 | 1.99 | 71.4 | 0.257 | 0.027 | 37.24 | 9096 | 8.32 | 55 |  | 0 | 0 | 6.81 | -3.787 | 0.23 | 101
8/21/2025 01:15 | 8 | 19 | 2.75 | 8.133 | 2.194 | 7.1 | 56 | 1.99 | 71.4 | 0.257 | 0.027 | 37.24 | 9096 | 8.32 | 55 |  | 179.83 | 3.18 | 6.8 | -3.787 | 0.22 | 101
8/21/2025 01:30 | 9 | 19 | 2.75 | 8.18 | 2.422 | 7.13 | 56 | 1.99 | 71.4 | 0.257 | 0.027 | 37.24 | 9096 | 8.31 | 55 |  | 180.34 | 3.17 | 6.81 | -3.787 | 0.22 | 101
8/21/2025 01:45 | 10 | 19 | 2.75 | 8.202 | 2.231 | 7.14 | 56 | 1.99 | 71.4 | 0.257 | 0.027 | 37.24 | 9096 | 8.31 | 55 |  | 180.15 | 3.16 | 6.82 | -3.787 | 0.22 | 101
8/21/2025 02:00 | 11 | 19 | 2.75 | 7.769 | 2.073 | 7.15 | 56 | 1.99 | 71.2 | 0.257 | 0.027 | 36.01 | 8921 | 8.3 | 58 |  | 180.09 | 3.34 | 6.83 | -3.787 | 0.21 | 101
8/21/2025 02:15 | 12 | 19 | 2.75 | 7.62 | 2.093 | 7.14 | 56 | 1.99 | 71.2 | 0.257 | 0.028 | 36.01 | 8921 | 8.3 | 58 |  | 180.07 | 3.4 | 6.82 | -3.787 | 0.21 | 101
8/21/2025 02:30 | 9 | 19 | 2.75 | 8.011 | 2.119 | 7.14 | 56 | 1.99 | 71.2 | 0.257 | 0.028 | 36.01 | 8921 | 8.29 | 58 |  | 179.96 | 3.23 | 6.82 | -3.787 | 0.22 | 101
8/21/2025 02:45 | 6 | 19 | 2.75 | 8.096 | 2.246 | 7.13 | 56 | 1.99 | 71.2 | 0.257 | 0.028 | 36.01 | 8921 | 8.29 | 58 |  | 179.32 | 3.19 | 6.81 | -3.787 | 0.21 | 101
8/21/2025 03:00 | 9 | 19 | 2.75 | 7.947 | 2.381 | 7.12 | 56 | 1.99 | 71.2 | 0.257 | 0.028 | 36.01 | 8921 | 8.28 | 58 |  | 179.7 | 3.26 | 6.8 | -3.787 | 0.22 | 101
8/21/2025 03:15 | 9 | 19 | 2.75 | 7.495 | 2.421 | 7.12 | 56 | 1.99 | 71.2 | 0.257 | 0.027 | 36.01 | 8921 | 8.3 | 58 |  | 179.88 | 3.46 | 6.8 | -3.787 | 0.25 | 101
8/21/2025 03:30 | 4 | 19 | 2.75 | 7.528 | 2.407 | 7.12 | 56 | 1.99 | 71.2 | 0.257 | 0.027 | 36.01 | 8921 | 8.34 | 58 |  | 179.77 | 3.44 | 6.8 | -3.787 | 0.21 | 101
8/21/2025 03:45 | 9 | 19 | 2.75 | 7.858 | 2.334 | 7.11 | 56 | 1.99 | 71.2 | 0.257 | 0.027 | 36.01 | 8921 | 8.39 | 58 |  | 180.09 | 3.3 | 6.8 | -3.787 | 0.21 | 101
8/21/2025 04:00 | 9 | 19 | 2.75 | 7.838 | 2.271 | 7.11 | 56 | 1.99 | 71.2 | 0.245 | 0.027 | 36.01 | 8921 | 8.4 | 58 |  | 179.7 | 3.3 | 6.79 | -3.787 | 0.2 | 101
8/21/2025 04:15 | 8 | 19 | 2.75 | 7.851 | 2.292 | 7.11 | 56 | 1.99 | 71.2 | 0.245 | 0.027 | 36.01 | 8921 | 8.4 | 58 |  | 179.63 | 3.29 | 6.79 | -3.787 | 0.21 | 101
8/21/2025 04:30 | 7 | 19 | 2.75 | 7.933 | 2.27 | 7.11 | 56 | 1.99 | 71.2 | 0.245 | 0.027 | 36.01 | 8921 | 8.39 | 58 |  | 179.68 | 3.26 | 6.79 | -3.787 | 0.2 | 101
8/21/2025 04:45 | 8 | 19 | 2.75 | 7.836 | 2.38 | 7.1 | 56 | 1.99 | 71.2 | 0.245 | 0.027 | 36.01 | 8921 | 8.38 | 58 |  | 179.6 | 3.3 | 6.79 | -3.787 | 0.22 | 101
8/21/2025 05:00 | 6 | 19 | 2.75 | 7.5 | 2.468 | 7.09 | 56 | 1.99 | 71.2 | 0.245 | 0.027 | 36.01 | 8921 | 8.36 | 58 |  | 179.63 | 3.45 | 6.78 | -3.787 | 0.2 | 101
8/21/2025 05:15 | 9 | 19 | 2.75 | 7.44 | 2.48 | 7.1 | 56 | 1.99 | 71.2 | 0.245 | 0.026 | 36.01 | 8921 | 8.35 | 58 |  | 179.85 | 3.48 | 6.79 | -3.787 | 0.22 | 101
8/21/2025 05:30 | 7 | 19 | 2.75 | 7.912 | 2.472 | 7.1 | 56 | 1.99 | 71.2 | 0.245 | 0.026 | 36.01 | 8921 | 8.34 | 58 |  | 179.6 | 3.27 | 6.8 | -3.787 | 0.21 | 101
8/21/2025 05:45 | 4 | 19 | 2.75 | 7.885 | 2.446 | 7.11 | 56 | 1.99 | 71.2 | 0.245 | 0.026 | 36.01 | 8921 | 8.33 | 58 |  | 179.5 | 3.28 | 6.81 | -3.787 | 0.21 | 101
8/21/2025 06:00 | 11 | 19 | 2.75 | 7.879 | 2.436 | 7.11 | 56 | 1.99 | 71.2 | 0.245 | 0.026 | 36.01 | 8921 | 8.33 | 58 |  | 179.07 | 3.27 | 6.81 | -3.787 | 0.21 | 101
8/21/2025 06:15 | 7 | 19 | 2.75 | 7.934 | 2.481 | 7.11 | 56 | 1.99 | 71.2 | 0.245 | 0.026 | 36.01 | 8921 | 8.32 | 58 |  | 179.48 | 3.26 | 6.81 | -3.787 | 0.21 | 101
8/21/2025 06:30 | 8 | 19 | 2.75 | 7.87 | 2.549 | 7.11 | 56 | 1.99 | 71.2 | 0.245 | 0.026 | 36.01 | 8921 | 8.32 | 58 |  | 179.4 | 3.28 | 6.81 | -3.787 | 0.21 | 101
8/21/2025 06:45 | 6 | 19 | 2.75 | 7.84 | 2.556 | 7.11 | 56 | 1.99 | 71.2 | 0.245 | 0.026 | 36.01 | 8921 | 8.31 | 58 |  | 179.62 | 3.3 | 6.81 | -3.787 | 0.21 | 101
8/21/2025 07:00 | 10 | 19 | 2.75 | 7.519 | 2.486 | 7.12 | 56 | 1.99 | 71.2 | 0.245 | 0.026 | 36.01 | 8921 | 8.31 | 58 |  | 179.04 | 3.43 | 6.82 | -3.787 | 0.2 | 101
8/21/2025 07:15 | 10 | 21 | 2.75 | 7.58 | 2.571 | 7.12 | 56 | 1.99 | 71.2 | 0.245 | 0.025 | 36.01 | 8921 | 8.31 | 58 |  | 179.19 | 3.4 | 6.81 | -3.787 | 0.2 | 101
8/21/2025 07:30 | 12 | 21 | 2.75 | 7.748 | 2.639 | 7.13 | 56 | 1.99 | 71.2 | 0.245 | 0.025 | 36.01 | 8921 | 8.31 | 58 |  | 179.18 | 3.33 | 6.8 | -3.787 | 0.21 | 101
8/21/2025 07:45 | 17 | 21 | 2.75 | 8.003 | 2.676 | 7.13 | 56 | 1.99 | 71.2 | 0.245 | 0.025 | 36.01 | 8921 | 8.3 | 58 |  | 178.69 | 3.22 | 6.8 | -3.787 | 0.2 | 100
8/21/2025 08:00 | 10 | 21 | 2.75 | 8.012 | 39.933 | 7.19 | 56 | 1.99 | 71.2 | 0.242 | 0.025 | 36.01 | 8921 | 8.3 | 58 |  | 178.95 | 3.22 | 6.8 | -3.787 | 0.23 | 101
8/21/2025 08:15 | 15 | 21 | 2.75 | 8.068 | 2.492 | 7.12 | 56 | 1.99 | 71.2 | 0.242 | 0.025 | 36.01 | 8921 | 8.3 | 58 |  | 179.37 | 3.2 | 6.8 | -3.787 | 0.21 | 100
8/21/2025 08:30 | 16 | 21 | 2.75 | 7.806 | 2.685 | 7.14 | 56 | 1.99 | 71.2 | 0.242 | 0.025 | 36.01 | 8921 | 8.29 | 58 |  | 179.02 | 3.3 | 6.8 | -3.787 | 0.19 | 100
8/21/2025 08:45 | 10 | 21 | 2.75 | 7.677 | 2.451 | 7.14 | 56 | 1.99 | 71.2 | 0.242 | 0.025 | 36.01 | 8921 | 8.29 | 58 |  | 0 | 0 | 6.8 | -3.787 | 0.19 | 101
8/21/2025 09:00 | 13 | 21 | 2.75 | 7.492 | 2.796 | 7.16 | 56 | 1.99 | 71.2 | 0.242 | 0.025 | 36.01 | 8921 | 8.29 | 58 |  | 0 | 0 | 6.81 | -3.787 | 0.19 | 101
8/21/2025 09:15 | 11 | 21 | 2.75 | 7.993 | 2.72 | 7.16 | 56 | 1.99 | 71.2 | 0.242 | 0.025 | 36.01 | 8921 | 8.28 | 58 |  | 0 | 0 | 6.81 | -3.787 | 0.2 | 101
8/21/2025 09:30 | 9 | 21 | 2.75 | 7.945 | 2.687 | 7.17 | 56 | 1.99 | 71.2 | 0.242 | 0.025 | 36.01 | 8921 | 8.28 | 58 |  | 0 | 0 | 6.81 | -3.787 | 0.2 | 101
8/21/2025 09:45 | 13 | 21 | 2.75 | 7.936 | 2.866 | 7.16 | 56 | 1.99 | 71.2 | 0.242 | 0.025 | 36.01 | 8921 | 8.28 | 58 |  | 0 | 0 | 6.81 | -3.787 | 0.21 | 101
8/21/2025 10:00 | 13 | 21 | 2.75 | 7.747 | 2.998 | 7.16 | 53 | 1.99 | 71.2 | 0.242 | 0.025 | 36.01 | 8921 | 8.28 | 58 |  | 0 | 0 | 6.81 | -3.787 | 0.2 | 101
8/21/2025 10:15 | 14 | 17 | 2.75 | 7.428 | 2.945 | 7.16 | 53 | 1.99 | 71.2 | 0.242 | 0.024 | 36.01 | 8921 | 8.28 | 58 |  | 177.11 | 3.43 | 6.81 | -3.787 | 0.23 | 101
8/21/2025 10:30 | 0 | 17 | 2.75 | 8.093 | 2.475 | 7.15 | 53 | 1.99 | 71.2 | 0.242 | 0.024 | 36.01 | 8921 | 8.28 | 58 |  | 177.61 | 3.16 | 6.82 | -3.787 | 0.2 | 101
8/21/2025 10:45 | -5 | 17 | 2.75 | 8.049 | 2.187 | 7.16 | 53 | 1.99 | 71.2 | 0.242 | 0.024 | 36.01 | 8921 | 8.28 | 58 |  | 177.38 | 3.17 | 6.8 | -3.787 | 0.33 | 101
8/21/2025 11:00 | -3 | 17 | 2.75 | 8.064 | 2.103 | 7.16 | 53 | 1.99 | 71.2 | 0.242 | 0.024 | 36.01 | 8921 | 8.29 | 58 |  | 177.32 | 3.17 | 6.73 | -3.787 | 0.2 | 101
8/21/2025 11:15 | -11 | 17 | 2.75 | 8.081 | 2.004 | 7.16 | 53 | 1.99 | 71.2 | 0.242 | 0.024 | 36.01 | 8921 | 8.29 | 58 |  | 177.17 | 3.16 | 6.71 | -3.787 | 0.21 | 101
8/21/2025 11:30 | -6 | 17 | 2.75 | 7.872 | 1.834 | 7.17 | 53 | 1.99 | 71.2 | 0.242 | 0.024 | 36.01 | 8921 | 8.3 | 58 |  | 176.88 | 3.24 | 6.72 | -3.787 | 0.2 | 101
8/21/2025 11:45 | -2 | 19 | 2.75 | 7.667 | 1.798 | 7.17 | 53 | 1.99 | 71.2 | 0.242 | 0.024 | 36.01 | 8921 | 8.3 | 58 |  | 177.58 | 3.34 | 6.72 | -3.787 | 0.32 | 101
8/21/2025 12:00 | 6 | 19 | 2.75 | 7.741 | 1.818 | 7.16 | 53 | 1.99 | 71.2 | 0.17 | 0.024 | 36.01 | 8921 | 8.3 | 58 |  | 177.6 | 3.3 | 6.72 | -3.659 | 0.2 | 101
8/21/2025 12:15 | 6 | 19 | 2.75 | 8.067 | 1.888 | 7.16 | 53 | 1.99 | 71.2 | 0.17 | 0.024 | 36.01 | 8921 | 8.3 | 58 |  | 177.14 | 3.16 | 6.7 | -3.659 | 0.19 | 101
8/21/2025 12:30 | 5 | 19 | 2.75 | 8.025 | 2.014 | 7.15 | 53 | 1.99 | 71.2 | 0.17 | 0.024 | 36.01 | 8921 | 8.3 | 58 |  | 176.8 | 3.17 | 6.69 | -3.659 | 0.19 | 101
8/21/2025 12:45 | 5 | 19 | 2.75 | 7.972 | 2.151 | 7.14 | 53 | 1.99 | 71.2 | 0.17 | 0.024 | 36.01 | 8921 | 8.3 | 58 |  | 177.12 | 3.2 | 6.68 | -3.659 | 0.19 | 101
8/21/2025 13:00 | 6 | 19 | 2.75 | 7.51 | 2.179 | 7.14 | 53 | 1.99 | 71.2 | 0.17 | 0.024 | 36.01 | 8921 | 8.3 | 58 |  | 177.31 | 3.4 | 6.68 | -3.659 | 0.18 | 101
8/21/2025 13:15 | 6 | 19 | 2.75 | 7.598 | 2.134 | 7.16 | 53 | 1.99 | 71.2 | 0.17 | 0.024 | 36.01 | 8921 | 8.3 | 58 |  | 177.54 | 3.36 | 6.68 | -3.659 | 0.2 | 101
8/21/2025 13:30 | 7 | 19 | 2.75 | 7.966 | 2.092 | 7.17 | 53 | 1.99 | 71.2 | 0.17 | 0.024 | 36.01 | 8921 | 8.3 | 58 |  | 177.66 | 3.21 | 6.68 | -3.659 | 0.2 | 101
8/21/2025 13:45 | 5 | 19 | 2.75 | 7.966 | 2.069 | 7.16 | 53 | 1.99 | 71.2 | 0.17 | 0.024 | 36.01 | 8921 | 8.3 | 58 |  | 177.61 | 3.21 | 6.68 | -3.659 | 0.25 | 101
8/21/2025 14:00 | 3 | 19 | 2.75 | 7.905 | 2.213 | 7.15 | 53 | 1.99 | 71.6 | 0.17 | 0.024 | 36.01 | 8921 | 8.3 | 55 |  | 177.64 | 3.24 | 6.68 | -3.659 | 0.19 | 101
8/21/2025 14:15 | 8 | 19 | 2.75 | 7.543 | 2.205 | 7.15 | 53 | 1.99 | 71.6 | 0.17 | 0.024 | 36.01 | 8921 | 8.29 | 55 |  | 177.27 | 3.38 | 6.68 | -3.659 | 0.18 | 101
8/21/2025 14:30 | 9 | 19 | 2.75 | 7.537 | 2.151 | 7.15 | 53 | 1.99 | 71.6 | 0.17 | 0.024 | 36.01 | 8921 | 8.29 | 55 |  | 177.63 | 3.39 | 6.67 | -3.659 | 0.21 | 101
8/21/2025 14:45 | 4 | 19 | 2.75 | 7.823 | 2.084 | 7.16 | 53 | 1.99 | 71.6 | 0.17 | 0.024 | 36.01 | 8921 | 8.29 | 55 |  | 177.88 | 3.27 | 6.67 | -3.659 | 0.2 | 101
8/21/2025 15:00 | 8 | 19 | 2.75 | 7.894 | 1.978 | 7.18 | 53 | 1.99 | 71.6 | 0.17 | 0.024 | 36.01 | 8921 | 8.28 | 55 |  | 177.45 | 3.24 | 6.66 | -3.659 | 0.21 | 101
8/21/2025 15:15 | 8 | 19 | 2.75 | 7.845 | 2.159 | 7.18 | 53 | 1.99 | 71.6 | 0.17 | 0.024 | 36.01 | 8921 | 8.28 | 55 |  | 177.1 | 3.25 | 6.66 | -3.659 | 0.21 | 101
8/21/2025 15:30 | 7 | 19 | 2.75 | 7.864 | 2.299 | 7.15 | 53 | 1.99 | 71.6 | 0.17 | 0.024 | 36.01 | 8921 | 8.27 | 55 |  | 177.56 | 3.25 | 6.66 | -3.659 | 0.19 | 101
8/21/2025 15:45 | 9 | 19 | 2.75 | 7.874 | 2.454 | 7.13 | 53 | 1.99 | 71.6 | 0.17 | 0.024 | 36.01 | 8921 | 8.27 | 55 |  | 177.14 | 3.24 | 6.66 | -3.659 | 0.19 | 101
8/21/2025 16:00 | 9 | 19 | 2.75 | 7.697 | 2.541 | 7.13 | 53 | 1.99 | 71.6 | 0.122 | 0.024 | 36.01 | 8921 | 8.27 | 55 |  | 0 | 0 | 6.66 | -3.659 | 0.19 | 101
8/21/2025 16:15 | 9 | 19 | 2.75 | 7.691 | 2.885 | 7.19 | 53 | 1.99 | 71.6 | 0.122 | 0.024 | 36.01 | 8921 | 8.26 | 55 |  | 0 | 0 | 6.65 | -3.659 | 0.21 | 101
8/21/2025 16:30 | 4 | 19 | 2.75 | 7.82 | 2.999 | 7.2 | 53 | 1.99 | 71.6 | 0.122 | 0.024 | 36.01 | 8921 | 8.26 | 55 |  | 0 | 0 | 6.65 | -3.659 | 0.2 | 101
8/21/2025 16:45 | 7 | 19 | 2.75 | 7.866 | 2.931 | 7.22 | 53 | 1.99 | 71.6 | 0.122 | 0.024 | 36.01 | 8921 | 8.27 | 55 |  | 0 | 0 | 6.65 | -3.659 | 0.21 | 101
8/21/2025 17:00 | 9 | 19 | 2.75 | 7.746 | 2.741 | 7.21 | 53 | 1.99 | 71.6 | 0.122 | 0.024 | 36.01 | 8921 | 8.27 | 55 |  | 0 | 0 | 6.64 | -3.659 | 0.2 | 101
8/21/2025 17:15 | 9 | 19 | 2.75 | 7.258 | 2.633 | 7.22 | 53 | 1.99 | 71.6 | 0.122 | 0.024 | 36.01 | 8921 | 8.27 | 55 |  | 0 | 0 | 6.64 | -3.659 | 0.26 | 101
8/21/2025 17:30 | 10 | 19 | 2.75 | 7.353 | 2.571 | 7.23 | 53 | 1.99 | 71.6 | 0.122 | 0.024 | 36.01 | 8921 | 8.28 | 55 |  | 0 | 0 | 6.64 | -3.659 | 0.2 | 101
8/21/2025 17:45 | 9 | 19 | 2.75 | 7.694 | 2.584 | 7.22 | 53 | 1.99 | 71.6 | 0.122 | 0.024 | 36.01 | 8921 | 8.29 | 55 |  | 0 | 0 | 6.64 | -3.659 | 0.22 | 101
8/21/2025 18:00 | 8 | 19 | 2.75 | 7.72 | 2.713 | 7.21 | 53 | 1.99 | 71.4 | 0.122 | 0.024 | 36.01 | 8921 | 8.31 | 55 |  | 0 | 0 | 6.65 | -3.659 | 0.2 | 101
8/21/2025 18:15 | 8 | 19 | 2.75 | 7.219 | 2.816 | 7.21 | 53 | 1.99 | 71.4 | 0.122 | 0.024 | 36.01 | 8921 | 8.34 | 55 |  | 0 | 0 | 6.65 | -3.659 | 0.23 | 101
8/21/2025 18:30 | 10 | 19 | 2.75 | 7.189 | 2.779 | 7.23 | 53 | 1.99 | 71.4 | 0.122 | 0.024 | 36.01 | 8921 | 8.35 | 55 |  | 0 | 0 | 6.65 | -3.659 | 0.22 | 101
8/21/2025 18:45 | 10 | 19 | 2.75 | 7.372 | 2.683 | 7.24 | 53 | 1.99 | 71.4 | 0.122 | 0.024 | 36.01 | 8921 | 8.37 | 55 |  | 0 | 0 | 6.64 | -3.659 | 0.22 | 101
8/21/2025 19:00 | 9 | 19 | 2.75 | 7.668 | 2.553 | 7.25 | 53 | 1.99 | 71.4 | 0.122 | 0.024 | 36.01 | 8921 | 8.38 | 55 |  | 0 | 0 | 6.64 | -3.659 | 0.21 | 101
8/21/2025 19:15 | 9 | 19 | 2.75 | 7.687 | 2.56 | 7.24 | 53 | 1.99 | 71.4 | 0.122 | 0.024 | 36.01 | 8921 | 8.39 | 55 |  | 0 | 0 | 6.64 | -3.659 | 0.21 | 101
8/21/2025 19:30 | 8 | 19 | 2.75 | 7.658 | 2.49 | 7.24 | 53 | 1.99 | 71.4 | 0.122 | 0.024 | 36.01 | 8921 | 8.4 | 55 |  | 0 | 0 | 6.63 | -3.659 | 0.24 | 101
8/21/2025 19:45 | 6 | 19 | 2.75 | 7.609 | 2.574 | 7.22 | 53 | 1.99 | 71.4 | 0.122 | 0.024 | 36.01 | 8921 | 8.4 | 55 |  | 0 | 0 | 6.63 | -3.659 | 0.23 | 101
8/21/2025 20:00 | 7 | 19 | 2.75 | 7.427 | 2.633 | 7.21 | 53 | 1.99 | 71.4 | 0.194 | 0.024 | 36.13 | 8912 | 8.4 | 55 |  | 0 | 0 | 6.63 | -3.659 | 0.21 | 101
8/21/2025 20:15 | 4 | 19 | 2.75 | 7.442 | 2.644 | 7.2 | 53 | 1.99 | 71.4 | 0.194 | 0.025 | 36.13 | 8912 | 8.4 | 55 |  | 0 | 0 | 6.62 | -3.659 | 0.22 | 101
8/21/2025 20:30 | 5 | 19 | 2.75 | 7.84 | 2.78 | 7.19 | 53 | 1.99 | 71.4 | 0.194 | 0.025 | 36.13 | 8912 | 8.4 | 55 |  | 0 | 0 | 6.62 | -3.659 | 0.23 | 101
8/21/2025 20:45 | 4 | 19 | 2.75 | 7.947 | 2.845 | 7.19 | 53 | 1.99 | 71.4 | 0.194 | 0.026 | 36.13 | 8912 | 8.4 | 55 |  | 0 | 0 | 6.62 | -3.659 | 0.24 | 101
8/21/2025 21:00 | 4 | 19 | 2.75 | 7.963 | 2.782 | 7.2 | 53 | 1.99 | 71.4 | 0.194 | 0.026 | 36.13 | 8912 | 8.39 | 55 |  | 0 | 0 | 6.61 | -3.659 | 0.24 | 101
8/21/2025 21:15 | 6 | 19 | 2.75 | 7.256 | 2.552 | 7.22 | 53 | 1.99 | 71.4 | 0.194 | 0.026 | 36.13 | 8912 | 8.36 | 55 |  | 0 | 0 | 6.6 | -3.659 | 0.21 | 101
8/21/2025 21:30 | 4 | 19 | 2.75 | 7.308 | 2.289 | 7.19 | 53 | 1.99 | 71.4 | 0.194 | 0.026 | 36.13 | 8912 | 8.33 | 55 |  | 177.8 | 3.5 | 6.6 | -3.659 | 0.21 | 101
8/21/2025 21:45 | 0 | 19 | 2.75 | 7.836 | 12.897 | 7.18 | 53 | 1.99 | 71.4 | 0.194 | 0.026 | 36.13 | 8912 | 8.33 | 55 |  | 178.04 | 3.27 | 6.6 | -3.659 | 0.23 | 101
8/21/2025 22:00 | 3 | 19 | 2.75 | 8.138 | 4.062 | 7.17 | 55 | 1.99 | 71.2 | 0.194 | 0.025 | 36.13 | 8912 | 8.35 | 55 |  | 178.1 | 3.15 | 6.6 | -3.659 | 0.2 | 101
8/21/2025 22:15 | 1 | 19 | 2.75 | 8.089 | 3.282 | 7.16 | 55 | 1.99 | 71.2 | 0.194 | 0.026 | 36.66 | 8948 | 8.36 | 55 |  | 177.96 | 3.17 | 6.6 | -3.659 | 0.21 | 101
8/21/2025 22:30 | 4 | 19 | 2.75 | 8.066 | 2.983 | 7.16 | 55 | 1.99 | 71.2 | 0.194 | 0.027 | 36.66 | 8948 | 8.36 | 55 |  | 177.84 | 3.17 | 6.61 | -3.659 | 0.21 | 101
8/21/2025 22:45 | 5 | 19 | 2.75 | 8.08 | 2.605 | 7.16 | 55 | 1.99 | 71.2 | 0.194 | 0.027 | 36.66 | 8948 | 8.36 | 55 |  | 177.92 | 3.17 | 6.61 | -3.659 | 0.22 | 101
8/21/2025 23:00 | 7 | 19 | 2.75 | 7.591 | 2.201 | 7.16 | 55 | 1.99 | 71.2 | 0.194 | 0.027 | 36.66 | 8948 | 8.35 | 55 |  | 177.98 | 3.38 | 6.61 | -3.659 | 0.21 | 101
8/21/2025 23:15 | 9 | 19 | 2.75 | 7.604 | 2.125 | 7.16 | 55 | 1.99 | 71.2 | 0.194 | 0.027 | 36.66 | 8948 | 8.35 | 55 |  | 177.82 | 3.37 | 6.61 | -3.659 | 0.19 | 101
8/21/2025 23:30 | 8 | 19 | 2.75 | 8.027 | 2.076 | 7.14 | 55 | 1.99 | 71.2 | 0.194 | 0.027 | 36.66 | 8948 | 8.37 | 55 |  | 177.81 | 3.19 | 6.61 | -3.659 | 0.22 | 101
8/21/2025 23:45 | 7 | 19 | 2.75 | 8.01 | 2.229 | 7.14 | 55 | 1.99 | 71.2 | 0.194 | 0.027 | 36.66 | 8948 | 8.4 | 55 |  | 177.82 | 3.2 | 6.62 | -3.659 | 0.21 | 101
8/22/2025 00:00 | 6 | 19 | 2.75 | 8.049 | 2.053 | 7.14 | 55 | 1.99 | 71.2 | 0.293 | 0.027 | 36.66 | 8948 | 8.44 | 55 | 1.53 | 177.49 | 3.18 | 6.62 | -3.659 | 0.25 | 101
8/22/2025 00:15 | 7 | 19 | 2.75 | 8.032 | 2.013 | 7.14 | 55 | 1.99 | 71.2 | 0.293 | 0.026 | 36.66 | 8948 | 8.45 | 55 | 1.53 | 177.01 | 3.17 | 6.61 | -3.659 | 0.2 | 101
8/22/2025 00:30 | 4 | 19 | 2.75 | 7.966 | 2.137 | 7.13 | 55 | 1.99 | 71.2 | 0.293 | 0.026 | 36.66 | 8948 | 8.45 | 55 | 1.53 | 177.5 | 3.21 | 6.61 | -3.659 | 0.21 | 101
8/22/2025 00:45 | 5 | 19 | 2.75 | 7.585 | 2.04 | 7.13 | 55 | 1.99 | 71.2 | 0.293 | 0.026 | 36.66 | 8948 | 8.44 | 55 | 1.53 | 176.73 | 3.36 | 6.61 | -3.659 | 0.24 | 101
8/22/2025 01:00 | 5 | 19 | 2.75 | 7.651 | 2.063 | 7.13 | 55 | 1.99 | 71.2 | 0.293 | 0.026 | 36.66 | 8948 | 8.42 | 55 | 1.53 | 177.69 | 3.34 | 6.6 | -3.659 | 0.19 | 101
8/22/2025 01:15 | 5 | 19 | 2.75 | 7.925 | 2.009 | 7.14 | 55 | 1.99 | 71.2 | 0.293 | 0.026 | 36.66 | 8948 | 8.41 | 55 | 1.53 | 177.64 | 3.23 | 6.6 | -3.659 | 0.2 | 101
8/22/2025 01:30 | 5 | 19 | 2.75 | 7.928 | 2.219 | 7.13 | 55 | 1.99 | 71.2 | 0.293 | 0.026 | 36.66 | 8948 | 8.4 | 55 | 1.53 | 177.03 | 3.22 | 6.59 | -3.659 | 0.19 | 101
8/22/2025 01:45 | 0 | 19 | 2.75 | 7.906 | 2.443 | 7.12 | 55 | 1.99 | 71.2 | 0.293 | 0.026 | 36.66 | 8948 | 8.4 | 55 | 1.53 | 177.03 | 3.22 | 6.58 | -3.659 | 0.19 | 101
8/22/2025 02:00 | 1 | 19 | 2.75 | 7.885 | 2.49 | 7.11 | 55 | 1.99 | 71.2 | 0.293 | 0.026 | 36.66 | 8948 | 8.4 | 58 | 1.53 | 176.99 | 3.23 | 6.58 | -3.659 | 0.19 | 101
8/22/2025 02:15 | 0 | 19 | 2.75 | 7.953 | 2.569 | 7.11 | 55 | 1.99 | 71.2 | 0.293 | 0.026 | 36.66 | 8948 | 8.4 | 58 | 1.53 | 177.26 | 3.21 | 6.59 | -3.659 | 0.2 | 101
8/22/2025 02:30 | 0 | 19 | 2.75 | 7.898 | 2.566 | 7.12 | 55 | 1.99 | 71.2 | 0.293 | 0.026 | 36.66 | 8948 | 8.39 | 58 | 1.53 | 176.93 | 3.23 | 6.59 | -3.659 | 0.2 | 101
8/22/2025 02:45 | -6 | 19 | 2.75 | 7.939 | 2.476 | 7.12 | 55 | 1.99 | 71.2 | 0.293 | 0.025 | 36.66 | 8948 | 8.39 | 58 | 1.53 | 176.64 | 3.2 | 6.59 | -3.659 | 0.19 | 101
8/22/2025 03:00 | 2 | 19 | 2.75 | 7.725 | 2.24 | 7.13 | 55 | 1.99 | 71.2 | 0.293 | 0.025 | 36.66 | 8948 | 8.39 | 58 | 1.53 | 176.72 | 3.29 | 6.6 | -3.659 | 0.19 | 101
8/22/2025 03:15 | 5 | 19 | 2.75 | 7.573 | 2.169 | 7.14 | 55 | 1.99 | 71.2 | 0.293 | 0.025 | 36.66 | 8948 | 8.39 | 58 | 1.53 | 0 | 0 | 6.6 | -3.659 | 0.19 | 101
8/22/2025 03:30 | 2 | 19 | 2.75 | 8.15 | 2.169 | 7.14 | 55 | 1.99 | 71.2 | 0.293 | 0.025 | 36.66 | 8948 | 8.39 | 58 | 1.53 | 180.61 | 3.19 | 6.6 | -3.659 | 0.19 | 101
8/22/2025 03:45 | -6 | 19 | 2.75 | 8.125 | 2.11 | 7.14 | 55 | 1.99 | 71.2 | 0.293 | 0.025 | 36.75 | 8956 | 8.39 | 58 | 1.53 | 180.86 | 3.21 | 6.61 | -3.659 | 0.18 | 101
8/22/2025 04:00 | 5 | 19 | 2.75 | 8.285 | 2.242 | 7.13 | 55 | 1.99 | 71.2 | 0.352 | 0.027 | 36.75 | 8956 | 8.39 | 58 | 1.53 | 181.03 | 3.15 | 6.62 | -3.659 | 0.19 | 101
8/22/2025 04:15 | 3 | 19 | 2.75 | 8.173 | 2.273 | 7.12 | 55 | 1.99 | 71.2 | 0.352 | 0.027 | 36.75 | 8956 | 8.4 | 58 | 1.53 | 180.73 | 3.18 | 6.63 | -3.659 | 0.17 | 101
8/22/2025 04:30 | -1 | 19 | 2.75 | 8.13 | 2.395 | 7.12 | 55 | 1.99 | 71.2 | 0.352 | 0.027 | 36.75 | 8956 | 8.39 | 58 | 1.53 | 180.51 | 3.2 | 6.63 | -3.659 | 0.18 | 101
8/22/2025 04:45 | 5 | 19 | 2.75 | 7.25 | 2.524 | 7.12 | 55 | 1.99 | 71.2 | 0.352 | 0.027 | 36.75 | 8956 | 8.37 | 58 | 1.53 | 177.2 | 3.52 | 6.64 | -3.659 | 0.19 | 101
8/22/2025 05:00 | -5 | 19 | 2.75 | 7.94 | 2.544 | 7.11 | 55 | 1.99 | 71.2 | 0.352 | 0.027 | 36.75 | 8956 | 8.35 | 58 | 1.53 | 180.46 | 3.27 | 6.65 | -3.659 | 0.19 | 101
8/22/2025 05:15 | 1 | 19 | 2.75 | 7.921 | 2.499 | 7.11 | 55 | 1.99 | 71.2 | 0.352 | 0.026 | 36.75 | 8956 | 8.35 | 58 | 1.53 | 180.4 | 3.28 | 6.65 | -3.659 | 0.17 | 101
8/22/2025 05:30 | 3 | 19 | 2.75 | 7.88 | 2.552 | 7.1 | 55 | 1.99 | 71.2 | 0.352 | 0.026 | 36.75 | 8956 | 8.36 | 58 | 1.53 | 180.53 | 3.3 | 6.65 | -3.659 | 0.16 | 101
8/22/2025 05:45 | 1 | 19 | 2.75 | 7.872 | 2.53 | 7.1 | 55 | 1.99 | 71.2 | 0.352 | 0.026 | 36.75 | 8956 | 8.37 | 58 | 1.53 | 180.85 | 3.31 | 6.64 | -3.659 | 0.19 | 101
8/22/2025 06:00 | 2 | 19 | 2.75 | 8.009 | 2.563 | 7.09 | 55 | 1.99 | 71.2 | 0.352 | 0.026 | 36.75 | 8956 | 8.37 | 58 | 1.53 | 180.57 | 3.25 | 6.63 | -3.659 | 0.16 | 101
8/22/2025 06:15 | 0 | 19 | 2.75 | 7.91 | 2.571 | 7.09 | 55 | 1.99 | 71.2 | 0.352 | 0.026 | 36.75 | 8956 | 8.37 | 58 | 1.53 | 180.41 | 3.28 | 6.64 | -3.659 | 0.19 | 101
8/22/2025 06:30 | 0 | 19 | 2.75 | 7.902 | 2.611 | 7.09 | 55 | 1.99 | 71.2 | 0.352 | 0.026 | 36.75 | 8956 | 8.36 | 58 | 1.53 | 180.63 | 3.29 | 6.64 | -3.659 | 0.17 | 101
8/22/2025 06:45 | -1 | 19 | 2.75 | 7.871 | 2.507 | 7.1 | 55 | 1.99 | 71.2 | 0.352 | 0.026 | 36.75 | 8956 | 8.36 | 58 | 1.53 | 179.96 | 3.29 | 6.65 | -3.659 | 0.16 | 101
8/22/2025 07:00 | 1 | 19 | 2.75 | 7.913 | 2.499 | 7.09 | 55 | 1.99 | 71.2 | 0.352 | 0.026 | 36.75 | 8956 | 8.35 | 58 | 1.53 | 180.39 | 3.28 | 6.66 | -3.659 | 0.17 | 101
8/22/2025 07:15 | 0 | 19 | 2.75 | 7.86 | 2.486 | 7.1 | 55 | 1.99 | 71.2 | 0.352 | 0.025 | 36.75 | 8956 | 8.35 | 58 | 1.53 | 180.42 | 3.31 | 6.66 | -3.659 | 0.23 | 101
8/22/2025 07:30 | 0 | 19 | 2.75 | 7.863 | 2.447 | 7.1 | 55 | 1.99 | 71.2 | 0.352 | 0.025 | 36.75 | 8956 | 8.35 | 58 | 1.53 | 180.14 | 3.3 | 6.67 | -3.659 | 0.21 | 101
8/22/2025 07:45 | 0 | 19 | 2.75 | 7.807 | 2.563 | 7.1 | 55 | 1.99 | 71.2 | 0.352 | 0.025 | 36.75 | 8956 | 8.34 | 58 | 1.53 | 180.18 | 3.32 | 6.67 | -3.659 | 0.19 | 101
8/22/2025 08:00 | 4 | 19 | 2.75 | 7.958 | 2.563 | 7.1 | 55 | 1.99 | 71.2 | 0.35 | 0.025 | 36.75 | 8956 | 8.34 | 58 | 1.53 | 180.17 | 3.26 | 6.65 | -3.659 | 0.17 | 101
8/22/2025 08:15 | 0 | 19 | 2.75 | 8.014 | 10.216 | 7.08 | 55 | 1.99 | 71.2 | 0.35 | 0.025 | 36.75 | 8956 | 8.33 | 58 | 1.53 | 180.43 | 3.24 | 6.65 | -3.659 | 0.2 | 101
8/22/2025 08:30 | 0 | 19 | 2.75 | 7.933 | 2.288 | 7.09 | 55 | 1.99 | 71.2 | 0.35 | 0.025 | 36.75 | 8956 | 8.33 | 58 | 1.53 | 179.94 | 3.27 | 6.65 | -3.659 | 0.21 | 101
8/22/2025 08:45 | 0 | 19 | 2.75 | 7.447 | 2.206 | 7.1 | 55 | 1.99 | 71.2 | 0.35 | 0.025 | 36.75 | 8956 | 8.33 | 58 | 1.53 | 180.24 | 3.49 | 6.65 | -3.659 | 0.17 | 101
8/22/2025 09:00 | -6 | 19 | 2.75 | 7.434 | 2.046 | 7.11 | 55 | 1.99 | 71.2 | 0.35 | 0.025 | 36.75 | 8956 | 8.33 | 58 | 1.53 | 180.13 | 3.49 | 6.65 | -3.659 | 0.17 | 101
8/22/2025 09:15 | 0 | 19 | 2.75 | 7.916 | 2.009 | 7.11 | 55 | 1.99 | 71.2 | 0.35 | 0.025 | 36.75 | 8956 | 8.33 | 58 | 1.53 | 179.74 | 3.27 | 6.65 | -3.659 | 0.19 | 101
8/22/2025 09:30 | 2 | 19 | 2.75 | 7.951 | 1.977 | 7.11 | 55 | 1.99 | 71.2 | 0.35 | 0.025 | 36.75 | 8956 | 8.32 | 58 | 1.53 | 180.14 | 3.26 | 6.65 | -3.659 | 0.17 | 101
8/22/2025 09:45 | -6 | 19 | 2.75 | 7.864 | 1.938 | 7.12 | 55 | 1.99 | 71.2 | 0.35 | 0.025 | 36.75 | 8956 | 8.31 | 58 | 1.53 | 180.33 | 3.3 | 6.65 | -3.659 | 0.17 | 101
8/22/2025 10:00 | 0 | 19 | 2.75 | 7.909 | 2.003 | 7.12 | 57 | 1.99 | 71 | 0.35 | 0.025 | 36.75 | 8956 | 8.31 | 58 | 1.53 | 180.11 | 3.28 | 6.65 | -3.659 | 0.17 | 101
8/22/2025 10:15 | -4 | 19 | 2.75 | 7.271 | 2.013 | 7.12 | 57 | 1.99 | 71 | 0.35 | 0.025 | 36.75 | 8956 | 8.32 | 58 | 1.53 | 177.92 | 3.52 | 6.88 | -3.659 | 0.16 | 101
8/22/2025 10:30 | -7 | 19 | 2.75 | 7.734 | 2.004 | 7.12 | 57 | 1.99 | 71 | 0.35 | 0.025 | 36.75 | 8956 | 8.32 | 58 | 1.53 | 180.16 | 3.35 | 6.76 | -3.659 | 0.26 | 101
8/22/2025 10:45 | 6 | 19 | 2.75 | 7.704 | 1.915 | 7.12 | 57 | 1.99 | 71 | 0.35 | 0.025 | 36.75 | 8956 | 8.32 | 58 | 1.53 | 180.75 | 3.38 | 6.76 | -3.659 | 0.25 | 101
8/22/2025 11:00 | 8 | 19 | 2.75 | 7.685 | 1.842 | 7.13 | 57 | 1.99 | 71 | 0.35 | 0.025 | 36.75 | 8956 | 8.32 | 58 | 1.53 | 180.54 | 3.38 | 6.81 | -3.659 | 0.25 | 101
8/22/2025 11:15 | 10 | 19 | 2.75 | 7.706 | 1.807 | 7.12 | 57 | 1.99 | 71 | 0.35 | 0.024 | 36.75 | 8956 | 8.32 | 58 | 1.53 | 179.64 | 3.36 | 6.87 | -3.659 | 0.27 | 101
8/22/2025 11:30 | 8 | 19 | 2.75 | 7.701 | 1.81 | 7.13 | 57 | 1.99 | 71 | 0.35 | 0.024 | 36.75 | 8956 | 8.32 | 58 | 1.53 | 180.15 | 3.37 | 6.87 | -3.659 | 0.26 | 101
8/22/2025 11:45 | 10 | 19 | 2.75 | 7.945 | 1.895 | 7.13 | 57 | 1.99 | 71 | 0.35 | 0.025 | 36.75 | 8956 | 8.33 | 58 | 1.53 | 180.3 | 3.27 | 6.86 | -3.659 | 0.26 | 101
8/22/2025 12:00 | 7 | 19 | 2.75 | 7.894 | 1.798 | 7.12 | 57 | 1.99 | 71 | 0.203 | 0.025 | 36.23 | 8865 | 8.33 | 58 | 1.53 | 180.6 | 3.29 | 6.86 | -3.882 | 0.26 | 101
8/22/2025 12:15 | 8 | 19 | 2.75 | 7.925 | 1.902 | 7.15 | 57 | 1.99 | 71 | 0.203 | 0.026 | 36.23 | 8865 | 8.33 | 58 | 1.53 | 0 | 0 | 6.87 | -3.882 | 0.26 | 101
8/22/2025 12:30 | 6 | 19 | 2.75 | 7.897 | 2.19 | 7.17 | 57 | 1.99 | 71 | 0.203 | 0.027 | 36.23 | 8865 | 8.34 | 58 | 1.53 | 0 | 0 | 6.86 | -3.882 | 0.26 | 101
8/22/2025 12:45 | 7 | 19 | 2.75 | 7.897 | 2.304 | 7.17 | 57 | 1.99 | 71 | 0.203 | 0.027 | 36.23 | 8865 | 8.34 | 58 | 1.53 | 177.33 | 3.23 | 6.86 | -3.882 | 0.25 | 101
8/22/2025 13:00 | 8 | 19 | 2.75 | 7.889 | 2.055 | 7.14 | 57 | 1.99 | 71 | 0.203 | 0.027 | 36.23 | 8865 | 8.34 | 58 | 1.53 | 177.74 | 3.24 | 6.85 | -3.882 | 0.26 | 101
8/22/2025 13:15 | 3 | 19 | 2.75 | 7.904 | 2.317 | 7.11 | 57 | 1.99 | 71 | 0.203 | 0.026 | 36.23 | 8865 | 8.34 | 58 | 1.53 | 177.42 | 3.23 | 6.82 | -3.882 | 0.24 | 101
8/22/2025 13:30 | 4 | 19 | 2.75 | 7.318 | 2.23 | 7.11 | 57 | 1.99 | 71 | 0.203 | 0.026 | 36.23 | 8865 | 8.37 | 58 | 1.53 | 177.94 | 3.5 | 6.82 | -3.882 | 0.26 | 101
8/22/2025 13:45 | 8 | 19 | 2.75 | 7.327 | 2.241 | 7.11 | 57 | 1.99 | 71 | 0.203 | 0.026 | 36.23 | 8865 | 8.41 | 58 | 1.53 | 177.04 | 3.48 | 6.82 | -3.882 | 0.24 | 101
8/22/2025 14:00 | 3 | 19 | 2.75 | 7.705 | 2.187 | 7.12 | 57 | 1.99 | 71.2 | 0.203 | 0.026 | 36.23 | 8865 | 8.43 | 57 | 1.53 | 177.53 | 3.32 | 6.83 | -3.882 | 0.25 | 101
8/22/2025 14:15 | 8 | 19 | 2.75 | 7.742 | 2.123 | 7.12 | 57 | 1.99 | 71.2 | 0.203 | 0.026 | 36.23 | 8865 | 8.44 | 57 | 1.53 | 177.7 | 3.31 | 6.83 | -3.882 | 0.27 | 101
8/22/2025 14:30 | 8 | 19 | 2.75 | 7.742 | 1.942 | 7.13 | 57 | 1.99 | 71.2 | 0.203 | 0.026 | 36.23 | 8865 | 8.43 | 57 | 1.53 | 177.46 | 3.3 | 6.84 | -3.882 | 0.26 | 101
8/22/2025 14:45 | 11 | 19 | 2.75 | 7.644 | 1.938 | 7.14 | 57 | 1.99 | 71.2 | 0.203 | 0.026 | 36.23 | 8865 | 8.42 | 57 | 1.53 | 177.33 | 3.34 | 6.84 | -3.882 | 0.26 | 101
8/22/2025 15:00 | 7 | 19 | 2.75 | 7.662 | 1.955 | 7.13 | 57 | 1.99 | 71.2 | 0.203 | 0.026 | 36.23 | 8865 | 8.41 | 57 | 1.53 | 178.13 | 3.35 | 6.83 | -3.882 | 0.27 | 101
8/22/2025 15:15 | 1 | 19 | 2.75 | 7.653 | 1.963 | 7.13 | 57 | 1.99 | 71.2 | 0.203 | 0.026 | 36.23 | 8865 | 8.4 | 57 | 1.53 | 177.33 | 3.34 | 6.83 | -3.882 | 0.25 | 101
8/22/2025 15:30 | 3 | 19 | 2.75 | 7.676 | 1.902 | 7.13 | 57 | 1.99 | 71.2 | 0.203 | 0.026 | 36.23 | 8865 | 8.39 | 57 | 1.53 | 177.37 | 3.33 | 6.85 | -3.882 | 0.26 | 101
8/22/2025 15:45 | 8 | 19 | 2.75 | 7.669 | 1.974 | 7.13 | 57 | 1.99 | 71.2 | 0.203 | 0.026 | 36.76 | 8979 | 8.38 | 57 | 1.53 | 177.09 | 3.33 | 6.84 | -3.882 | 0.27 | 101
8/22/2025 16:00 | 2 | 19 | 2.75 | 7.717 | 1.873 | 7.14 | 57 | 1.99 | 71.2 | 0.202 | 0.027 | 36.76 | 8979 | 8.37 | 57 | 1.53 | 180.07 | 3.36 | 6.84 | -3.882 | 0.25 | 101
8/22/2025 16:15 | 4 | 19 | 2.75 | 7.731 | 1.89 | 7.14 | 57 | 1.99 | 71.2 | 0.202 | 0.028 | 36.76 | 8979 | 8.37 | 57 | 1.53 | 180.32 | 3.36 | 6.84 | -3.882 | 0.25 | 101
8/22/2025 16:30 | 8 | 19 | 2.75 | 7.722 | 1.923 | 7.13 | 57 | 1.99 | 71.2 | 0.202 | 0.028 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 180.71 | 3.37 | 6.84 | -3.882 | 0.26 | 101
8/22/2025 16:45 | 10 | 19 | 2.75 | 7.741 | 1.876 | 7.14 | 57 | 1.99 | 71.2 | 0.202 | 0.028 | 36.76 | 8979 | 8.34 | 57 | 1.53 | 180.38 | 3.36 | 6.84 | -3.882 | 0.25 | 101
8/22/2025 17:00 | 8 | 19 | 2.75 | 7.702 | 1.866 | 7.14 | 57 | 1.99 | 71.2 | 0.202 | 0.028 | 36.76 | 8979 | 8.33 | 57 | 1.53 | 180.8 | 3.38 | 6.85 | -3.882 | 0.26 | 101
8/22/2025 17:15 | 8 | 19 | 2.75 | 7.674 | 1.889 | 7.14 | 57 | 1.99 | 71.2 | 0.202 | 0.027 | 36.76 | 8979 | 8.33 | 57 | 1.53 | 180.23 | 3.38 | 6.85 | -3.882 | 0.26 | 101
8/22/2025 17:30 | 11 | 19 | 2.75 | 7.696 | 1.846 | 7.14 | 57 | 1.99 | 71.2 | 0.202 | 0.027 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 180.62 | 3.38 | 6.85 | -3.882 | 0.26 | 101
8/22/2025 17:45 | 9 | 19 | 2.75 | 7.682 | 1.913 | 7.14 | 57 | 1.99 | 71.2 | 0.202 | 0.027 | 36.76 | 8979 | 8.39 | 57 | 1.53 | 180.54 | 3.38 | 6.84 | -3.882 | 0.28 | 101
8/22/2025 18:00 | 12 | 19 | 2.75 | 7.737 | 1.882 | 7.14 | 57 | 1.99 | 71.4 | 0.202 | 0.027 | 36.76 | 8979 | 8.4 | 57 | 1.53 | 181.08 | 3.37 | 6.84 | -3.882 | 0.25 | 101
8/22/2025 18:15 | 13 | 19 | 2.75 | 7.772 | 1.935 | 7.14 | 57 | 1.99 | 71.4 | 0.202 | 0.027 | 36.76 | 8979 | 8.4 | 57 | 1.53 | 180.48 | 3.34 | 6.83 | -3.882 | 0.27 | 98
8/22/2025 18:30 | 13 | 19 | 2.75 | 7.792 | 1.99 | 7.13 | 57 | 1.99 | 71.4 | 0.202 | 0.027 | 36.76 | 8979 | 8.4 | 57 | 1.53 | 180.47 | 3.34 | 6.83 | -3.882 | 0.26 | 97
8/22/2025 18:45 | 13 | 19 | 2.75 | 7.726 | 1.995 | 7.13 | 57 | 1.99 | 71.4 | 0.202 | 0.027 | 36.76 | 8979 | 8.39 | 57 | 1.53 | 180.9 | 3.37 | 6.83 | -3.882 | 0.25 | 99
8/22/2025 19:00 | 10 | 19 | 2.75 | 7.749 | 1.946 | 7.14 | 57 | 1.99 | 71.4 | 0.202 | 0.027 | 36.76 | 8979 | 8.38 | 57 | 1.53 | 180.57 | 3.36 | 6.83 | -3.882 | 0.26 | 101
8/22/2025 19:15 | 11 | 19 | 2.75 | 7.725 | 1.993 | 7.12 | 57 | 1.99 | 71.4 | 0.202 | 0.028 | 36.76 | 8979 | 8.37 | 57 | 1.53 | 180.58 | 3.37 | 6.82 | -3.882 | 0.26 | 101
8/22/2025 19:30 | 10 | 19 | 2.75 | 7.738 | 1.985 | 7.12 | 57 | 1.99 | 71.4 | 0.202 | 0.028 | 36.76 | 8979 | 8.37 | 57 | 1.53 | 179.71 | 3.34 | 6.81 | -3.882 | 0.25 | 101
8/22/2025 19:45 | 10 | 19 | 2.75 | 7.72 | 1.949 | 7.12 | 57 | 1.99 | 71.4 | 0.202 | 0.028 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 181.34 | 3.38 | 6.82 | -3.882 | 0.26 | 101
8/22/2025 20:00 | 11 | 19 | 2.75 | 7.387 | 1.891 | 7.13 | 57 | 1.99 | 71.4 | 0.318 | 0.028 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 179.77 | 3.5 | 6.83 | -3.882 | 0.26 | 101
8/22/2025 20:15 | 9 | 19 | 2.75 | 7.423 | 1.859 | 7.12 | 57 | 1.99 | 71.4 | 0.318 | 0.027 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 179.71 | 3.49 | 6.83 | -3.882 | 0.26 | 101
8/22/2025 20:30 | 10 | 19 | 2.75 | 7.743 | 1.893 | 7.12 | 57 | 1.99 | 71.4 | 0.318 | 0.027 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 179.71 | 3.34 | 6.82 | -3.882 | 0.25 | 101
8/22/2025 20:45 | 4 | 19 | 2.75 | 7.716 | 1.914 | 7.11 | 57 | 1.99 | 71.4 | 0.318 | 0.027 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 179.84 | 3.36 | 6.82 | -3.882 | 0.25 | 101
8/22/2025 21:00 | 6 | 19 | 2.75 | 7.758 | 1.935 | 7.11 | 57 | 1.99 | 71.4 | 0.318 | 0.027 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 180.41 | 3.35 | 6.82 | -3.882 | 0.24 | 101
8/22/2025 21:15 | 6 | 19 | 2.75 | 7.757 | 1.991 | 7.11 | 57 | 1.99 | 71.4 | 0.318 | 0.027 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 180.51 | 3.35 | 6.81 | -3.882 | 0.25 | 101
8/22/2025 21:30 | 9 | 19 | 2.75 | 7.707 | 2 | 7.11 | 57 | 1.99 | 71.4 | 0.318 | 0.027 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 179.78 | 3.36 | 6.81 | -3.882 | 0.25 | 101
8/22/2025 21:45 | 2 | 19 | 2.75 | 7.363 | 2.004 | 7.11 | 57 | 1.99 | 71.4 | 0.318 | 0.027 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 178.53 | 3.49 | 6.82 | -3.882 | 0.25 | 101
8/22/2025 22:00 | 7 | 19 | 2.75 | 7.359 | 2.055 | 7.11 | 57 | 1.99 | 71.2 | 0.318 | 0.027 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 178.07 | 3.48 | 6.82 | -3.882 | 0.24 | 101
8/22/2025 22:15 | 5 | 19 | 2.75 | 7.534 | 1.983 | 7.12 | 57 | 1.99 | 71.2 | 0.318 | 0.027 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 178.29 | 3.41 | 6.83 | -3.882 | 0.25 | 101
8/22/2025 22:30 | 6 | 19 | 2.75 | 7.778 | 1.967 | 7.12 | 57 | 1.99 | 71.2 | 0.318 | 0.027 | 36.76 | 8979 | 8.36 | 57 | 1.53 | 178.41 | 3.3 | 6.83 | -3.882 | 0.25 | 101
8/22/2025 22:45 | 7 | 19 | 2.75 | 7.718 | 1.987 | 7.13 | 57 | 1.99 | 71.2 | 0.318 | 0.027 | 36.76 | 8979 | 8.35 | 57 | 1.53 | 178.45 | 3.33 | 6.83 | -3.882 | 0.25 | 101
8/22/2025 23:00 | 8 | 19 | 2.75 | 7.161 | 1.955 | 7.13 | 57 | 1.99 | 71.2 | 0.318 | 0.027 | 36.76 | 8979 | 8.35 | 57 | 1.53 | 177.99 | 3.58 | 6.83 | -3.882 | 0.25 | 101
8/22/2025 23:15 | 7 | 19 | 2.75 | 7.223 | 1.982 | 7.12 | 57 | 1.99 | 71.2 | 0.318 | 0.027 | 36.76 | 8979 | 8.35 | 57 | 1.53 | 178.51 | 3.56 | 6.83 | -3.882 | 0.25 | 101
8/22/2025 23:30 | 7 | 19 | 2.75 | 7.777 | 1.998 | 7.12 | 57 | 1.99 | 71.2 | 0.318 | 0.027 | 36.76 | 8979 | 8.35 | 57 | 1.53 | 178.11 | 3.3 | 6.83 | -3.882 | 0.24 | 101
8/22/2025 23:45 | 7 | 19 | 2.75 | 7.748 | 2.026 | 7.11 | 57 | 1.99 | 71.2 | 0.318 | 0.027 | 36.76 | 8979 | 8.35 | 57 | 1.53 | 178.05 | 3.31 | 6.82 | -3.882 | 0.25 | 101
8/23/2025 00:00 | 5 | 19 | 2.75 | 8.032 | 2.12 | 7.11 | 57 | 1.96 | 71.2 | 0.291 | 0.027 | 36.76 | 8979 | 8.34 | 57 |  | 178.47 | 3.2 | 6.82 | -3.882 | 0.26 | 101
8/23/2025 00:15 | 4 | 19 | 2.75 | 8.053 | 2.12 | 7.11 | 57 | 1.96 | 71.2 | 0.291 | 0.027 | 36.76 | 8979 | 8.34 | 57 |  | 178.44 | 3.19 | 6.81 | -3.882 | 0.25 | 101
8/23/2025 00:30 | 4 | 19 | 2.75 | 8.055 | 2.183 | 7.1 | 57 | 1.96 | 71.2 | 0.291 | 0.027 | 36.76 | 8979 | 8.35 | 57 |  | 177.67 | 3.18 | 6.81 | -3.882 | 0.24 | 101
8/23/2025 00:45 | 4 | 19 | 2.75 | 7.405 | 2.166 | 7.11 | 57 | 1.96 | 71.2 | 0.291 | 0.027 | 36.76 | 8979 | 8.34 | 57 |  | 177.84 | 3.46 | 6.83 | -3.882 | 0.25 | 101
8/23/2025 01:00 | 2 | 19 | 2.75 | 7.422 | 2.18 | 7.11 | 57 | 1.96 | 71.2 | 0.291 | 0.027 | 36.76 | 8979 | 8.34 | 57 |  | 178.01 | 3.45 | 6.84 | -3.882 | 0.25 | 101
8/23/2025 01:15 | 8 | 19 | 2.75 | 7.472 | 2.223 | 7.11 | 57 | 1.96 | 71.2 | 0.291 | 0.026 | 36.76 | 8979 | 8.34 | 57 |  | 177.64 | 3.42 | 6.83 | -3.882 | 0.28 | 101
8/23/2025 01:30 | -2 | 19 | 2.75 | 7.737 | 2.17 | 7.11 | 57 | 1.96 | 71.2 | 0.291 | 0.026 | 36.76 | 8979 | 8.33 | 57 |  | 177.51 | 3.3 | 6.83 | -3.882 | 0.24 | 101
8/23/2025 01:45 | 4 | 19 | 2.75 | 7.73 | 2.201 | 7.1 | 57 | 1.96 | 71.2 | 0.291 | 0.026 | 36.76 | 8979 | 8.33 | 57 |  | 178.14 | 3.32 | 6.82 | -3.882 | 0.22 | 101
8/23/2025 02:00 | 1 | 19 | 2.75 | 7.216 | 2.15 | 7.1 | 57 | 1.96 | 71.2 | 0.291 | 0.026 | 36.76 | 8979 | 8.33 | 58 |  | 178.12 | 3.55 | 6.82 | -3.882 | 0.23 | 101
8/23/2025 02:15 | 2 | 19 | 2.75 | 6.993 | 2.095 | 7.1 | 57 | 1.96 | 71.2 | 0.291 | 0.026 | 36.76 | 8979 | 8.33 | 58 |  | 177.67 | 3.66 | 6.82 | -3.882 | 0.25 | 101
8/23/2025 02:30 | 4 | 19 | 2.75 | 7.508 | 2.066 | 7.1 | 57 | 1.96 | 71.2 | 0.291 | 0.026 | 36.76 | 8979 | 8.33 | 58 |  | 178.07 | 3.42 | 6.82 | -3.882 | 0.23 | 101
8/23/2025 02:45 | 2 | 19 | 2.75 | 7.426 | 1.968 | 7.11 | 57 | 1.96 | 71.2 | 0.291 | 0.026 | 36.76 | 8979 | 8.33 | 58 |  | 177.98 | 3.45 | 6.84 | -3.882 | 0.26 | 101
8/23/2025 03:00 | 1 | 19 | 2.75 | 7.448 | 1.937 | 7.11 | 57 | 1.96 | 71.2 | 0.291 | 0.026 | 36.76 | 8979 | 8.33 | 58 |  | 178.09 | 3.44 | 6.83 | -3.882 | 0.24 | 101
8/23/2025 03:15 | 3 | 19 | 2.75 | 7.568 | 1.94 | 7.11 | 57 | 1.96 | 71.2 | 0.291 | 0.026 | 36.76 | 8979 | 8.33 | 58 |  | 177.74 | 3.38 | 6.83 | -3.882 | 0.23 | 101
8/23/2025 03:30 | 6 | 19 | 2.75 | 6.908 | 1.893 | 7.12 | 57 | 1.96 | 71.2 | 0.291 | 0.026 | 36.76 | 8979 | 8.33 | 58 |  | 177.04 | 3.69 | 6.83 | -3.882 | 0.22 | 101
8/23/2025 03:45 | 7 | 19 | 2.75 | 6.934 | 1.93 | 7.11 | 57 | 1.96 | 71.2 | 0.291 | 0.025 | 36.76 | 8979 | 8.33 | 58 |  | 177.52 | 3.69 | 6.82 | -3.882 | 0.23 | 101
8/23/2025 04:00 | 6 | 19 | 2.75 | 7.509 | 1.946 | 7.11 | 57 | 1.96 | 71.2 | 0.298 | 0.025 | 36.76 | 8979 | 8.33 | 58 |  | 176.71 | 3.39 | 6.82 | -3.882 | 0.22 | 101
8/23/2025 04:15 | 1 | 19 | 2.75 | 7.43 | 1.975 | 7.11 | 57 | 1.96 | 71.2 | 0.298 | 0.026 | 36.76 | 8979 | 8.33 | 58 |  | 177.62 | 3.44 | 6.83 | -3.882 | 0.23 | 101
8/23/2025 04:30 | 7 | 19 | 2.75 | 7.461 | 1.948 | 7.11 | 57 | 1.96 | 71.2 | 0.298 | 0.025 | 36.76 | 8979 | 8.33 | 58 |  | 177.35 | 3.42 | 6.82 | -3.882 | 0.24 | 101
8/23/2025 04:45 | 4 | 19 | 2.75 | 7.498 | 1.956 | 7.1 | 57 | 1.96 | 71.2 | 0.298 | 0.025 | 36.76 | 8979 | 8.33 | 58 |  | 177.53 | 3.41 | 6.82 | -3.882 | 0.23 | 101
8/23/2025 05:00 | -4 | 19 | 2.75 | 7.449 | 1.927 | 7.1 | 57 | 1.96 | 71.2 | 0.298 | 0.025 | 36.76 | 8979 | 8.33 | 58 |  | 177.51 | 3.43 | 6.82 | -3.882 | 0.22 | 101
8/23/2025 05:15 | 4 | 19 | 2.75 | 6.898 | 1.872 | 7.11 | 57 | 1.96 | 71.2 | 0.298 | 0.025 | 36.76 | 8979 | 8.33 | 58 |  | 167.75 | 3.5 | 6.83 | -3.882 | 0.22 | 101
8/23/2025 05:30 | 2 | 19 | 2.75 | 7.217 | 1.925 | 7.1 | 57 | 1.96 | 71.2 | 0.298 | 0.025 | 36.76 | 8979 | 8.33 | 58 |  | 174.9 | 3.49 | 6.82 | -3.882 | 0.21 | 101
8/23/2025 05:45 | 4 | 19 | 2.75 | 7.567 | 2.048 | 7.1 | 57 | 1.96 | 71.2 | 0.298 | 0.025 | 36.76 | 8979 | 8.32 | 58 |  | 177.21 | 3.37 | 6.82 | -3.882 | 0.22 | 101
8/23/2025 06:00 | 3 | 19 | 2.75 | 7.474 | 2.278 | 7.1 | 57 | 1.96 | 71 | 0.298 | 0.025 | 36.76 | 8979 | 8.32 | 58 |  | 177 | 3.41 | 6.82 | -3.882 | 0.22 | 101
8/23/2025 06:15 | 2 | 19 | 2.75 | 7.385 | 2.366 | 7.11 | 57 | 1.96 | 71 | 0.298 | 0.025 | 36.76 | 8979 | 8.32 | 58 |  | 177.05 | 3.45 | 6.82 | -3.882 | 0.21 | 101
8/23/2025 06:30 | 0 | 19 | 2.75 | 7.088 | 2.176 | 7.12 | 57 | 1.96 | 71 | 0.298 | 0.025 | 36.76 | 8979 | 8.32 | 58 |  | 174.05 | 3.54 | 6.83 | -3.882 | 0.23 | 101
8/23/2025 06:45 | 0 | 19 | 2.75 | 6.747 | 2.116 | 7.13 | 57 | 1.96 | 71 | 0.298 | 0.025 | 36.76 | 8979 | 8.32 | 58 |  | 164.47 | 3.51 | 6.84 | -3.882 | 0.2 | 101
8/23/2025 07:00 | 3 | 19 | 2.75 | 7.254 | 2.019 | 7.13 | 57 | 1.96 | 71 | 0.298 | 0.025 | 36.76 | 8979 | 8.32 | 58 |  | 174.14 | 3.46 | 6.84 | -3.882 | 0.21 | 101
8/23/2025 07:15 | 1 | 19 | 2.75 | 7.252 | 1.831 | 7.14 | 57 | 1.96 | 71 | 0.298 | 0.025 | 36.76 | 8979 | 8.31 | 58 |  | 174.9 | 3.47 | 6.85 | -3.882 | 0.21 | 101
8/23/2025 07:30 | 4 | 19 | 2.75 | 7.174 | 1.809 | 7.14 | 57 | 1.96 | 71 | 0.298 | 0.025 | 36.76 | 8979 | 8.31 | 58 |  | 174.65 | 3.51 | 6.85 | -3.882 | 0.22 | 101
8/23/2025 07:45 | 2 | 19 | 2.75 | 7.363 | 1.885 | 7.14 | 57 | 1.96 | 71 | 0.298 | 0.025 | 36.76 | 8979 | 8.31 | 58 |  | 176.9 | 3.46 | 6.85 | -3.882 | 0.22 | 101
8/23/2025 08:00 | 2 | 19 | 2.75 | 7.356 | 1.868 | 7.14 | 57 | 1.96 | 71 | 0.255 | 0.025 | 36.76 | 8979 | 8.31 | 58 |  | 176.44 | 3.45 | 6.85 | -3.882 | 0.2 | 101
8/23/2025 08:15 | 1 | 19 | 2.75 | 7.325 | 1.891 | 7.13 | 57 | 1.96 | 71 | 0.255 | 0.024 | 36.76 | 8979 | 8.31 | 58 |  | 176.71 | 3.47 | 6.84 | -3.882 | 0.21 | 101
8/23/2025 08:30 | 0 | 19 | 2.75 | 7.299 | 10.144 | 7.13 | 57 | 1.96 | 71 | 0.255 | 0.024 | 36.76 | 8979 | 8.31 | 58 |  | 176.52 | 3.48 | 6.84 | -3.882 | 0.23 | 101
8/23/2025 08:45 | -4 | 19 | 2.75 | 6.914 | 2.67 | 7.13 | 57 | 1.96 | 71 | 0.255 | 0.024 | 36.76 | 8979 | 8.32 | 58 |  | 0 | 0 | 6.84 | -3.882 | 0.21 | 101
8/23/2025 09:00 | -3 | 19 | 2.75 | 6.9 | 2.636 | 7.14 | 57 | 1.96 | 71 | 0.255 | 0.024 | 36.76 | 8979 | 8.31 | 58 |  | 0 | 0 | 6.83 | -3.882 | 0.2 | 101
8/23/2025 09:15 | -6 | 19 | 2.75 | 7.277 | 2.534 | 7.15 | 57 | 1.96 | 71 | 0.255 | 0.024 | 36.76 | 8979 | 8.31 | 58 |  | 0 | 0 | 6.83 | -3.882 | 0.2 | 101
8/23/2025 09:30 | -11 | 19 | 2.75 | 7.233 | 2.485 | 7.16 | 57 | 1.96 | 71 | 0.255 | 0.024 | 36.76 | 8979 | 8.32 | 58 |  | 0 | 0 | 6.84 | -3.882 | 0.22 | 92
8/23/2025 09:45 | -5 | 19 | 2.75 | 7.072 | 2.279 | 7.17 | 57 | 1.96 | 71 | 0.255 | 0.024 | 36.76 | 8979 | 8.32 | 58 |  | 0 | 0 | 6.85 | -3.882 | 0.22 | 101
8/23/2025 10:00 | -1 | 19 | 2.75 | 6.657 | 2.167 | 7.18 | 56 | 1.96 | 71 | 0.255 | 0.024 | 36.76 | 8979 | 8.32 | 58 |  | 0 | 0 | 6.83 | -3.882 | 0.24 | 101
8/23/2025 10:15 | -2 | 19 | 2.75 | 6.714 | 2.182 | 7.17 | 56 | 1.96 | 71 | 0.255 | 0.024 | 36.74 | 9006 | 8.32 | 58 |  | 162.56 | 3.49 | 6.83 | -3.882 | 0.22 | 101
8/23/2025 10:30 | 0 | 19 | 2.75 | 7.08 | 1.825 | 7.14 | 56 | 1.96 | 71 | 0.255 | 0.025 | 36.74 | 9006 | 8.33 | 58 |  | 171.69 | 3.49 | 6.84 | -3.882 | 0.23 | 101
8/23/2025 10:45 | 0 | 19 | 2.75 | 7.138 | 1.671 | 7.14 | 56 | 1.96 | 71 | 0.255 | 0.026 | 36.74 | 9006 | 8.33 | 58 |  | 172 | 3.47 | 6.95 | -3.882 | 0.23 | 101
8/23/2025 11:00 | 3 | 19 | 2.75 | 7.075 | 1.567 | 7.15 | 56 | 1.96 | 71 | 0.255 | 0.026 | 36.74 | 9006 | 8.33 | 58 |  | 170.39 | 3.47 | 6.82 | -3.882 | 0.21 | 101
8/23/2025 11:15 | 2 | 19 | 2.75 | 7.075 | 1.514 | 7.15 | 56 | 1.96 | 71 | 0.255 | 0.026 | 36.74 | 9006 | 8.33 | 58 |  | 171.36 | 3.49 | 6.83 | -3.882 | 0.21 | 101
8/23/2025 11:30 | -14 | 19 | 2.75 | 7.041 | 1.532 | 7.15 | 56 | 1.96 | 71 | 0.255 | 0.026 | 36.74 | 9006 | 8.32 | 58 |  | 171.51 | 3.51 | 6.88 | -3.882 | 0.2 | 91
8/23/2025 11:45 | -1 | 19 | 2.75 | 7.028 | 1.566 | 7.14 | 56 | 1.96 | 71 | 0.255 | 0.026 | 36.74 | 9006 | 8.31 | 58 |  | 172.22 | 3.53 | 6.9 | -3.882 | 0.2 | 101
8/23/2025 12:00 | -8 | 19 | 2.75 | 6.813 | 1.66 | 7.14 | 56 | 1.96 | 71 | 0.211 | 0.026 | 36.74 | 9006 | 8.32 | 58 |  | 166.91 | 3.53 | 6.88 | -3.882 | 0.2 | 101
8/23/2025 12:15 | 0 | 19 | 2.75 | 6.453 | 1.639 | 7.14 | 56 | 1.96 | 71 | 0.211 | 0.026 | 36.74 | 9006 | 8.35 | 58 |  | 156.76 | 3.5 | 6.88 | -3.882 | 0.19 | 101
8/23/2025 12:30 | -2 | 19 | 2.75 | 6.619 | 2 | 7.13 | 56 | 1.96 | 71 | 0.211 | 0.026 | 36.74 | 9006 | 8.38 | 58 |  | 160.66 | 3.5 | 6.86 | -3.882 | 0.18 | 101
8/23/2025 12:45 | -4 | 19 | 2.75 | 6.645 | 2.41 | 7.11 | 56 | 1.96 | 71 | 0.211 | 0.025 | 36.74 | 9006 | 8.4 | 58 |  | 160.31 | 3.47 | 6.85 | -3.882 | 0.18 | 101
8/23/2025 13:00 | -3 | 19 | 2.75 | 6.783 | 2.647 | 7.11 | 56 | 1.96 | 71 | 0.211 | 0.025 | 36.74 | 9006 | 8.4 | 58 |  | 166.77 | 3.54 | 6.85 | -3.882 | 0.24 | 101
8/23/2025 13:15 | -9 | 19 | 2.75 | 6.87 | 2.414 | 7.13 | 56 | 1.96 | 71 | 0.211 | 0.025 | 36.74 | 9006 | 8.4 | 58 |  | 166.72 | 3.49 | 6.86 | -3.882 | 0.2 | 101
8/23/2025 13:30 | 4 | 19 | 2.75 | 6.806 | 2.18 | 7.14 | 56 | 1.96 | 71 | 0.211 | 0.025 | 36.74 | 9006 | 8.39 | 58 |  | 166.9 | 3.53 | 6.88 | -3.882 | 0.22 | 101
8/23/2025 13:45 | -2 | 19 | 2.75 | 6.899 | 2.037 | 7.14 | 56 | 1.96 | 71 | 0.211 | 0.025 | 36.74 | 9006 | 8.4 | 58 |  | 165.85 | 3.46 | 6.88 | -3.882 | 0.2 | 101
8/23/2025 14:00 | -5 | 19 | 2.75 | 6.239 | 1.876 | 7.14 | 56 | 1.96 | 71 | 0.211 | 0.025 | 36.74 | 9006 | 8.39 | 58 |  | 150.98 | 3.48 | 6.89 | -3.882 | 0.2 | 101
8/23/2025 14:15 | -7 | 19 | 2.75 | 6.285 | 1.791 | 7.14 | 56 | 1.96 | 71 | 0.211 | 0.025 | 36.74 | 9006 | 8.39 | 58 |  | 152.7 | 3.5 | 6.88 | -3.882 | 0.2 | 93
8/23/2025 14:30 | -4 | 19 | 2.75 | 6.936 | 1.668 | 7.14 | 56 | 1.96 | 71 | 0.211 | 0.025 | 36.74 | 9006 | 8.39 | 58 |  | 169.55 | 3.52 | 6.88 | -3.882 | 0.21 | 101
8/23/2025 14:45 | -3 | 19 | 2.75 | 6.977 | 1.635 | 7.14 | 56 | 1.96 | 71 | 0.211 | 0.025 | 36.74 | 9006 | 8.38 | 58 |  | 169.55 | 3.5 | 6.88 | -3.882 | 0.2 | 101
8/23/2025 15:00 | -1 | 19 | 2.75 | 6.989 | 1.544 | 7.15 | 56 | 1.96 | 71 | 0.211 | 0.025 | 36.74 | 9006 | 8.38 | 58 |  | 0 | 0 | 6.89 | -3.882 | 0.22 | 101
8/23/2025 15:15 | -3 | 19 | 2.75 | 6.929 | 1.628 | 7.16 | 56 | 1.96 | 71 | 0.211 | 0.025 | 36.74 | 9006 | 8.39 | 58 |  | 169.02 | 3.51 | 6.89 | -3.882 | 0.2 | 101
8/23/2025 15:30 | -5 | 19 | 2.75 | 5.763 | 6.792 | 7.15 | 56 | 1.96 | 71 | 0.211 | 0.025 | 36.74 | 9006 | 8.39 | 58 |  | 141.14 | 3.53 | 6.87 | -3.882 | 0.21 | 101
8/23/2025 15:45 | 0 | 19 | 2.75 | 5.123 | 2.945 | 7.14 | 56 | 1.96 | 71 | 0.211 | 0.025 | 36.93 | 8992 | 8.39 | 58 |  | 123.16 | 3.46 | 6.87 | -3.882 | 0.2 | 101
8/23/2025 16:00 | 0 | 19 | 2.75 | 5.658 | 2.311 | 7.13 | 56 | 1.96 | 71 | 0.161 | 0.025 | 36.93 | 8992 | 8.39 | 58 |  | 136.75 | 3.48 | 6.87 | -3.882 | 0.2 | 101
8/23/2025 16:15 | 0 | 19 | 2.75 | 5.688 | 2.088 | 7.12 | 56 | 1.96 | 71 | 0.161 | 0.025 | 36.93 | 8992 | 8.39 | 58 |  | 137.53 | 3.48 | 6.86 | -3.882 | 0.21 | 101
8/23/2025 16:30 | -3 | 19 | 2.75 | 5.645 | 2.41 | 7.1 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.39 | 58 |  | 137.3 | 3.5 | 6.83 | -3.882 | 0.19 | 101
8/23/2025 16:45 | -2 | 19 | 2.75 | 5.686 | 1.862 | 7.11 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.39 | 58 |  | 137.68 | 3.49 | 6.86 | -3.882 | 0.19 | 101
8/23/2025 17:00 | -4 | 19 | 2.75 | 5.691 | 2.033 | 7.11 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.4 | 58 |  | 137.48 | 3.48 | 6.85 | -3.882 | 0.19 | 101
8/23/2025 17:15 | -8 | 19 | 2.75 | 5.668 | 2.22 | 7.09 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.39 | 58 |  | 137.67 | 3.5 | 6.83 | -3.882 | 0.19 | 101
8/23/2025 17:30 | -3 | 19 | 2.75 | 5.665 | 2.31 | 7.09 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.38 | 58 |  | 137.49 | 3.49 | 6.83 | -3.882 | 0.18 | 101
8/23/2025 17:45 | -2 | 19 | 2.75 | 5.283 | 2.451 | 7.09 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.36 | 58 |  | 129.24 | 3.52 | 6.85 | -3.882 | 0.18 | 101
8/23/2025 18:00 | -2 | 19 | 2.75 | 5.289 | 2.585 | 7.09 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.36 | 58 |  | 127.32 | 3.47 | 6.85 | -3.882 | 0.18 | 101
8/23/2025 18:15 | -5 | 19 | 2.75 | 5.577 | 2.538 | 7.08 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.38 | 58 |  | 133.63 | 3.45 | 6.86 | -3.882 | 0.18 | 101
8/23/2025 18:30 | -4 | 19 | 2.75 | 5.752 | 2.652 | 7.08 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.4 | 58 |  | 142.56 | 3.57 | 6.84 | -3.882 | 0.18 | 101
8/23/2025 18:45 | -4 | 19 | 2.75 | 5.888 | 2.618 | 7.08 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.42 | 58 |  | 142.56 | 3.49 | 6.82 | -3.882 | 0.19 | 101
8/23/2025 19:00 | -6 | 19 | 2.75 | 5.066 | 2.492 | 7.08 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.43 | 58 |  | 123.32 | 3.51 | 6.82 | -3.882 | 0.2 | 101
8/23/2025 19:15 | 0 | 19 | 2.75 | 5.067 | 2.259 | 7.09 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.44 | 58 |  | 123.63 | 3.51 | 6.84 | -3.882 | 0.19 | 101
8/23/2025 19:30 | -2 | 19 | 2.75 | 5.516 | 2.101 | 7.1 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.46 | 58 |  | 134.51 | 3.51 | 6.86 | -3.882 | 0.2 | 101
8/23/2025 19:45 | -2 | 19 | 2.75 | 5.551 | 1.989 | 7.1 | 56 | 1.96 | 71 | 0.161 | 0.026 | 36.93 | 8992 | 8.46 | 58 |  | 133.76 | 3.47 | 6.87 | -3.882 | 0.2 | 101
8/23/2025 20:00 | -1 | 19 | 2.75 | 5.832 | 2.144 | 7.09 | 56 | 1.96 | 71 | 0.174 | 0.026 | 37.97 | 9135 | 8.47 | 58 |  | 141.47 | 3.49 | 6.85 | -3.882 | 0.17 | 101
8/23/2025 20:15 | -4 | 19 | 2.75 | 5.826 | 2.005 | 7.1 | 56 | 1.96 | 71 | 0.174 | 0.027 | 37.97 | 9135 | 8.48 | 58 |  | 140.18 | 3.46 | 6.84 | -3.882 | 0.21 | 101
8/23/2025 20:30 | -4 | 19 | 2.75 | 5.669 | 2.037 | 7.1 | 56 | 1.96 | 71 | 0.174 | 0.028 | 37.97 | 9135 | 8.48 | 58 |  | 137.26 | 3.49 | 6.83 | -3.882 | 0.2 | 101
8/23/2025 20:45 | -1 | 19 | 2.75 | 5.858 | 1.997 | 7.1 | 56 | 1.96 | 71 | 0.174 | 0.028 | 37.97 | 9135 | 8.49 | 58 |  | 140.9 | 3.46 | 6.83 | -3.882 | 0.2 | 101
8/23/2025 21:00 | -5 | 19 | 2.75 | 6.146 | 2.147 | 7.09 | 56 | 1.96 | 71 | 0.174 | 0.029 | 37.97 | 9135 | 8.49 | 58 |  | 149.66 | 3.51 | 6.82 | -3.882 | 0.19 | 101
8/23/2025 21:15 | -7 | 19 | 2.75 | 6.144 | 2.111 | 7.09 | 56 | 1.96 | 71 | 0.174 | 0.029 | 37.97 | 9135 | 8.49 | 58 |  | 148.28 | 3.48 | 6.81 | -3.882 | 0.22 | 101
8/23/2025 21:30 | -4 | 19 | 2.75 | 6.121 | 2.116 | 7.1 | 56 | 1.96 | 71 | 0.174 | 0.029 | 37.97 | 9135 | 8.47 | 58 |  | 148.46 | 3.49 | 6.83 | -3.882 | 0.2 | 101
8/23/2025 21:45 | -8 | 19 | 2.75 | 5.631 | 2.161 | 7.09 | 56 | 1.96 | 71 | 0.174 | 0.029 | 37.97 | 9135 | 8.45 | 58 |  | 136.66 | 3.49 | 6.83 | -3.882 | 0.17 | 101
8/23/2025 22:00 | -9 | 19 | 2.75 | 5.668 | 2.148 | 7.09 | 56 | 1.96 | 71 | 0.174 | 0.029 | 37.97 | 9135 | 8.46 | 58 |  | 137.19 | 3.49 | 6.82 | -3.882 | 0.22 | 101
8/23/2025 22:15 | -12 | 19 | 2.75 | 6.24 | 2.419 | 7.09 | 56 | 1.96 | 71 | 0.174 | 0.029 | 37.97 | 9135 | 8.47 | 58 |  | 0 | 0 | 6.82 | -3.882 | 0.17 | 92
8/23/2025 22:30 | -12 | 19 | 2.75 | 6.283 | 2.35 | 7.09 | 56 | 1.96 | 71 | 0.174 | 0.029 | 37.97 | 9135 | 8.48 | 58 |  | 152.33 | 3.49 | 6.84 | -3.882 | 0.18 | 90
8/23/2025 22:45 | -9 | 19 | 2.75 | 6.228 | 2.473 | 7.09 | 56 | 1.96 | 71 | 0.174 | 0.029 | 37.97 | 9135 | 8.49 | 58 |  | 150.96 | 3.49 | 6.84 | -3.882 | 0.17 | 95
8/23/2025 23:00 | -14 | 19 | 2.75 | 5.794 | 2.335 | 7.08 | 56 | 1.96 | 71 | 0.174 | 0.029 | 37.97 | 9135 | 8.5 | 58 |  | 140.64 | 3.5 | 6.83 | -3.882 | 0.32 | 89
8/23/2025 23:15 | -8 | 19 | 2.75 | 5.782 | 2.468 | 7.07 | 56 | 1.96 | 71 | 0.174 | 0.029 | 37.97 | 9135 | 8.5 | 58 |  | 141.35 | 3.52 | 6.81 | -3.882 | 0.27 | 101
8/23/2025 23:30 | -7 | 19 | 2.75 | 6.122 | 2.458 | 7.07 | 56 | 1.96 | 71 | 0.174 | 0.029 | 37.97 | 9135 | 8.48 | 58 |  | 148.41 | 3.49 | 6.81 | -3.882 | 0.22 | 101
8/23/2025 23:45 | -13 | 19 | 2.75 | 6.118 | 2.399 | 7.08 | 56 | 1.96 | 71 | 0.174 | 0.029 | 37.97 | 9135 | 8.47 | 58 |  | 148.34 | 3.49 | 6.81 | -3.882 | 0.23 | 86
8/24/2025 00:00 | -7 | 19 | 2.75 | 6.142 | 2.45 | 7.08 | 56 | 1.96 | 71 | 0.18 | 0.029 | 37.97 | 9135 | 8.46 | 58 |  | 149.31 | 3.5 | 6.82 | -3.882 | 0.21 | 101
8/24/2025 00:15 | -9 | 19 | 2.75 | 5.783 | 2.244 | 7.08 | 56 | 1.96 | 71 | 0.18 | 0.029 | 37.97 | 9135 | 8.46 | 58 |  | 142.03 | 3.54 | 6.82 | -3.882 | 0.27 | 101
8/24/2025 00:30 | -8 | 19 | 2.75 | 5.785 | 2.117 | 7.09 | 56 | 1.96 | 71 | 0.18 | 0.029 | 37.97 | 9135 | 8.45 | 58 |  | 140.23 | 3.49 | 6.83 | -3.882 | 0.22 | 101
8/24/2025 00:45 | -11 | 19 | 2.75 | 7.222 | 2.139 | 7.09 | 56 | 1.96 | 71 | 0.18 | 0.029 | 38.35 | 9154 | 8.46 | 58 |  | 175.27 | 3.49 | 6.84 | -3.882 | 0.2 | 89
8/24/2025 01:00 | -16 | 19 | 2.75 | 6.993 | 2.034 | 7.09 | 56 | 1.96 | 71 | 0.18 | 0.03 | 38.35 | 9154 | 8.45 | 58 |  | 170.99 | 3.52 | 6.85 | -3.882 | 0.22 | 84
8/24/2025 01:15 | -16 | 19 | 2.75 | 6.306 | 2.001 | 7.09 | 56 | 1.96 | 71 | 0.18 | 0.031 | 38.35 | 9154 | 8.45 | 58 |  | 153.69 | 3.51 | 6.84 | -3.882 | 0.2 | 83
8/24/2025 01:30 | -8 | 19 | 2.75 | 6.663 | 2.088 | 7.08 | 56 | 1.96 | 71 | 0.18 | 0.031 | 38.35 | 9154 | 8.45 | 58 |  | 163.47 | 3.53 | 6.82 | -3.882 | 0.23 | 101
8/24/2025 01:45 | -11 | 19 | 2.75 | 6.779 | 1.972 | 7.08 | 56 | 1.96 | 71 | 0.18 | 0.031 | 38.35 | 9154 | 8.44 | 58 |  | 163.27 | 3.47 | 6.82 | -3.882 | 0.21 | 90
8/24/2025 02:00 | -6 | 19 | 2.75 | 6.7 | 1.933 | 7.09 | 56 | 1.96 | 71 | 0.18 | 0.031 | 38.35 | 9154 | 8.43 | 58 |  | 162.28 | 3.49 | 6.83 | -3.882 | 0.19 | 101
8/24/2025 02:15 | -9 | 19 | 2.75 | 6.761 | 1.881 | 7.09 | 56 | 1.96 | 71 | 0.18 | 0.031 | 38.35 | 9154 | 8.41 | 58 |  | 162.32 | 3.46 | 6.84 | -3.882 | 0.2 | 101
8/24/2025 02:30 | -11 | 19 | 2.75 | 6.611 | 1.989 | 7.08 | 56 | 1.96 | 71 | 0.18 | 0.031 | 38.35 | 9154 | 8.43 | 58 |  | 161.59 | 3.52 | 6.82 | -3.882 | 0.19 | 91
8/24/2025 02:45 | -13 | 19 | 2.75 | 5.976 | 1.971 | 7.08 | 56 | 1.96 | 71 | 0.18 | 0.031 | 38.35 | 9154 | 8.45 | 58 |  | 145.07 | 3.5 | 6.81 | -3.882 | 0.2 | 87
8/24/2025 03:00 | -8 | 19 | 2.75 | 6.552 | 2.071 | 7.07 | 56 | 1.96 | 71 | 0.18 | 0.031 | 38.35 | 9154 | 8.46 | 58 |  | 158.24 | 3.48 | 6.81 | -3.882 | 0.21 | 101
8/24/2025 03:15 | -9 | 19 | 2.75 | 6.529 | 2.183 | 7.06 | 56 | 1.96 | 71 | 0.18 | 0.031 | 38.35 | 9154 | 8.47 | 58 |  | 156.81 | 3.46 | 6.81 | -3.882 | 0.18 | 92
8/24/2025 03:30 | -12 | 19 | 2.75 | 6.528 | 2.128 | 7.06 | 56 | 1.96 | 71 | 0.18 | 0.031 | 38.35 | 9154 | 8.45 | 58 |  | 160.7 | 3.54 | 6.83 | -3.882 | 0.21 | 89
8/24/2025 03:45 | -11 | 19 | 2.75 | 6.535 | 2.098 | 7.06 | 56 | 1.96 | 71 | 0.18 | 0.031 | 38.35 | 9154 | 8.43 | 58 |  | 159.18 | 3.51 | 6.84 | -3.882 | 0.22 | 90
8/24/2025 04:00 | -9 | 19 | 2.75 | 6.526 | 2.089 | 7.06 | 56 | 1.96 | 71 | 0.226 | 0.031 | 38.35 | 9154 | 8.42 | 58 |  | 180.13 | 3.97 | 6.83 | -3.882 | 0.21 | 92
8/24/2025 04:15 | -7 | 19 | 2.75 | 6.739 | 2.078 | 7.06 | 56 | 1.96 | 71 | 0.226 | 0.03 | 38.35 | 9154 | 8.4 | 58 |  | 179.5 | 3.84 | 6.82 | -3.882 | 0.2 | 101
8/24/2025 04:30 | -20 | 19 | 2.75 | 6.708 | 2.082 | 7.06 | 56 | 1.96 | 71 | 0.226 | 0.03 | 38.35 | 9154 | 8.39 | 58 |  | 180.18 | 3.87 | 6.82 | -3.882 | 0.29 | 80
8/24/2025 04:45 | -6 | 19 | 2.75 | 6.696 | 1.997 | 7.07 | 56 | 1.96 | 71 | 0.226 | 0.03 | 38.35 | 9154 | 8.38 | 58 |  | 179.93 | 3.87 | 6.82 | -3.882 | 0.26 | 101
8/24/2025 05:00 | -9 | 19 | 2.75 | 6.708 | 2.097 | 7.07 | 56 | 1.96 | 71 | 0.226 | 0.03 | 38.35 | 9154 | 8.37 | 58 |  | 180.13 | 3.87 | 6.82 | -3.882 | 0.21 | 101
8/24/2025 05:15 | -9 | 19 | 2.75 | 6.924 | 2.161 | 7.06 | 56 | 1.96 | 71 | 0.226 | 0.03 | 38.35 | 9154 | 8.36 | 58 |  | 180.18 | 3.75 | 6.81 | -3.882 | 0.21 | 101
8/24/2025 05:30 | -11 | 19 | 2.75 | 6.825 | 2.179 | 7.06 | 56 | 1.96 | 71 | 0.226 | 0.03 | 38.35 | 9154 | 8.36 | 58 |  | 180.03 | 3.8 | 6.81 | -3.882 | 0.2 | 91
8/24/2025 05:45 | -6 | 19 | 2.75 | 6.831 | 2.146 | 7.06 | 56 | 1.96 | 71 | 0.226 | 0.03 | 38.35 | 9154 | 8.35 | 58 |  | 180.1 | 3.8 | 6.81 | -3.882 | 0.2 | 101
8/24/2025 06:00 | -5 | 19 | 2.75 | 7.809 | 2.216 | 7.06 | 56 | 1.96 | 70.8 | 0.226 | 0.03 | 38.35 | 9154 | 8.35 | 58 |  | 179.44 | 3.31 | 6.81 | -3.882 | 0.22 | 101
8/24/2025 06:15 | -8 | 19 | 2.75 | 7.966 | 2.219 | 7.07 | 56 | 1.96 | 70.8 | 0.226 | 0.03 | 38.35 | 9154 | 8.34 | 58 |  | 179.43 | 3.24 | 6.79 | -3.882 | 0.19 | 101
8/24/2025 06:30 | -6 | 19 | 2.75 | 7.929 | 2.235 | 7.07 | 56 | 1.96 | 70.8 | 0.226 | 0.03 | 38.35 | 9154 | 8.34 | 58 |  | 178.1 | 3.23 | 6.79 | -3.882 | 0.2 | 101
8/24/2025 06:45 | -7 | 19 | 2.75 | 7.53 | 7.866 | 7.07 | 56 | 1.96 | 70.8 | 0.226 | 0.03 | 38.35 | 9154 | 8.34 | 58 |  | 178.4 | 3.41 | 6.81 | -3.882 | 0.19 | 101
8/24/2025 07:00 | -8 | 19 | 2.75 | 7.5 | 3.256 | 7.06 | 56 | 1.96 | 70.8 | 0.226 | 0.03 | 38.35 | 9154 | 8.34 | 58 |  | 178.02 | 3.42 | 6.81 | -3.882 | 0.19 | 101
8/24/2025 07:15 | -9 | 19 | 2.75 | 7.9 | 2.671 | 7.07 | 56 | 1.96 | 70.8 | 0.226 | 0.03 | 38.35 | 9154 | 8.34 | 58 |  | 177.92 | 3.24 | 6.82 | -3.882 | 0.2 | 93
8/24/2025 07:30 | -10 | 19 | 2.75 | 7.888 | 2.49 | 7.07 | 56 | 1.96 | 70.8 | 0.226 | 0.03 | 38.35 | 9154 | 8.34 | 58 |  | 177.76 | 3.25 | 6.81 | -3.882 | 0.2 | 90
8/24/2025 07:45 | -8 | 19 | 2.75 | 7.803 | 2.279 | 7.07 | 56 | 1.96 | 70.8 | 0.226 | 0.03 | 38.35 | 9154 | 8.36 | 58 |  | 177.87 | 3.28 | 6.82 | -3.882 | 0.18 | 101
8/24/2025 08:00 | -14 | 19 | 2.75 | 7.309 | 2.313 | 7.07 | 56 | 1.96 | 70.8 | 0.261 | 0.03 | 38.35 | 9154 | 8.37 | 58 |  | 177.83 | 3.5 | 6.83 | -3.882 | 0.19 | 87
8/24/2025 08:15 | -10 | 19 | 2.75 | 7.071 | 2.362 | 7.07 | 56 | 1.96 | 70.8 | 0.261 | 0.03 | 38.35 | 9154 | 8.37 | 58 |  | 177.8 | 3.62 | 6.83 | -3.882 | 0.21 | 92
8/24/2025 08:30 | -9 | 19 | 2.75 | 7.497 | 2.39 | 7.07 | 56 | 1.96 | 70.8 | 0.261 | 0.029 | 38.35 | 9154 | 8.36 | 58 |  | 177.74 | 3.41 | 6.82 | -3.882 | 0.17 | 101
8/24/2025 08:45 | -15 | 19 | 2.75 | 7.524 | 2.369 | 7.08 | 56 | 1.96 | 70.8 | 0.261 | 0.029 | 38.35 | 9154 | 8.35 | 58 |  | 177.37 | 3.39 | 6.82 | -3.882 | 0.18 | 83
8/24/2025 09:00 | -6 | 19 | 2.75 | 7.534 | 2.339 | 7.08 | 56 | 1.96 | 70.8 | 0.261 | 0.029 | 38.35 | 9154 | 8.33 | 58 |  | 177.78 | 3.4 | 6.82 | -3.882 | 0.17 | 101
8/24/2025 09:15 | -6 | 19 | 2.75 | 7.551 | 2.334 | 7.08 | 56 | 1.96 | 70.8 | 0.261 | 0.029 | 38.35 | 9154 | 8.32 | 58 |  | 177.99 | 3.39 | 6.83 | -3.882 | 0.16 | 101
8/24/2025 09:30 | -5 | 19 | 2.75 | 7.514 | 2.321 | 7.08 | 56 | 1.96 | 70.8 | 0.261 | 0.029 | 38.35 | 9154 | 8.31 | 58 |  | 177.29 | 3.4 | 6.83 | -3.882 | 0.2 | 101
8/24/2025 09:45 | -10 | 19 | 2.75 | 7.523 | 2.265 | 7.08 | 56 | 1.96 | 70.8 | 0.261 | 0.029 | 38.35 | 9154 | 8.31 | 58 |  | 177.77 | 3.4 | 6.83 | -3.882 | 0.17 | 93
8/24/2025 10:00 | -14 | 19 | 2.75 | 7.125 | 2.256 | 7.08 | 57 | 1.96 | 70.8 | 0.261 | 0.029 | 38.35 | 9154 | 8.3 | 58 |  | 177.8 | 3.59 | 6.83 | -3.882 | 0.17 | 87
8/24/2025 10:15 | -17 | 19 | 2.75 | 7.245 | 2.241 | 7.08 | 57 | 1.96 | 70.8 | 0.261 | 0.029 | 38.35 | 9154 | 8.3 | 58 |  | 177.41 | 3.53 | 6.83 | -3.882 | 0.18 | 83
8/24/2025 10:30 | -15 | 19 | 2.75 | 7.449 | 2.204 | 7.08 | 57 | 1.96 | 70.8 | 0.261 | 0.029 | 38.35 | 9154 | 8.29 | 58 |  | 177.92 | 3.44 | 6.83 | -3.882 | 0.18 | 85
8/24/2025 10:45 | -14 | 19 | 2.75 | 7.468 | 2.165 | 7.08 | 57 | 1.96 | 70.8 | 0.261 | 0.029 | 38.35 | 9154 | 8.29 | 58 |  | 177.07 | 3.41 | 6.86 | -3.882 | 0.2 | 87
8/24/2025 11:00 | -12 | 19 | 2.75 | 7.43 | 39.935 | 7.11 | 57 | 1.96 | 70.8 | 0.261 | 0.029 | 38.35 | 9154 | 8.29 | 58 |  | 177.08 | 3.43 | 6.79 | -3.882 | 0.18 | 88
8/24/2025 11:15 | -15 | 19 | 2.75 | 7.432 | 2.009 | 7.08 | 57 | 1.96 | 70.8 | 0.261 | 0.029 | 38.35 | 9154 | 8.29 | 58 |  | 178.12 | 3.45 | 6.8 | -3.882 | 0.18 | 83
8/24/2025 11:30 | -24 | 19 | 2.75 | 7.425 | 2.03 | 7.08 | 57 | 1.96 | 70.8 | 0.261 | 0.029 | 38.35 | 9154 | 8.29 | 58 |  | 177.64 | 3.45 | 6.86 | -3.882 | 0.17 | 74
8/24/2025 11:45 | -10 | 19 | 2.75 | 7.418 | 2.057 | 7.08 | 57 | 1.96 | 70.8 | 0.261 | 0.028 | 38.35 | 9154 | 8.3 | 58 |  | 177.1 | 3.44 | 6.87 | -3.882 | 0.17 | 90
8/24/2025 12:00 | -18 | 19 | 2.75 | 7.659 | 2.02 | 7.08 | 57 | 1.96 | 70.8 | 0.175 | 0.028 | 38.35 | 9154 | 8.3 | 58 |  | 177.86 | 3.34 | 6.85 | -3.882 | 0.18 | 81
8/24/2025 12:15 | -17 | 19 | 2.75 | 7.889 | 2.125 | 7.08 | 57 | 1.96 | 70.8 | 0.175 | 0.028 | 38.75 | 9153 | 8.3 | 58 |  | 177.34 | 3.24 | 6.84 | -3.882 | 0.19 | 82
8/24/2025 12:30 | -18 | 19 | 2.75 | 7.9 | 2.061 | 7.08 | 57 | 1.96 | 70.8 | 0.175 | 0.03 | 38.75 | 9153 | 8.31 | 58 |  | 177.7 | 3.24 | 6.83 | -3.882 | 0.17 | 81
8/24/2025 12:45 | -13 | 19 | 2.75 | 7.758 | 1.914 | 7.09 | 57 | 1.96 | 70.8 | 0.175 | 0.03 | 38.75 | 9153 | 8.3 | 58 |  | 177.41 | 3.29 | 6.84 | -3.882 | 0.17 | 88
8/24/2025 13:00 | -12 | 19 | 2.75 | 7.403 | 1.863 | 7.09 | 57 | 1.96 | 70.8 | 0.175 | 0.03 | 38.75 | 9153 | 8.31 | 58 |  | 177.29 | 3.45 | 6.84 | -3.882 | 0.19 | 90
8/24/2025 13:15 | -17 | 19 | 2.75 | 7.613 | 1.831 | 7.1 | 57 | 1.96 | 70.8 | 0.175 | 0.03 | 38.75 | 9153 | 8.29 | 58 |  | 177.23 | 3.35 | 6.86 | -3.882 | 0.21 | 82
8/24/2025 13:30 | -12 | 19 | 2.75 | 7.89 | 1.787 | 7.11 | 57 | 1.96 | 70.8 | 0.175 | 0.03 | 38.75 | 9153 | 8.29 | 58 |  | 177.15 | 3.23 | 6.86 | -3.882 | 0.2 | 91
8/24/2025 13:45 | -15 | 19 | 2.75 | 7.82 | 1.706 | 7.11 | 57 | 1.96 | 70.8 | 0.175 | 0.03 | 38.75 | 9153 | 8.31 | 58 |  | 177.37 | 3.27 | 6.86 | -3.882 | 0.18 | 84
8/24/2025 14:00 | -14 | 19 | 2.75 | 7.831 | 1.718 | 7.11 | 57 | 1.96 | 71 | 0.175 | 0.03 | 38.75 | 9153 | 8.34 | 58 |  | 177.05 | 3.26 | 6.86 | -3.882 | 0.16 | 87
8/24/2025 14:15 | -19 | 19 | 2.75 | 7.853 | 1.692 | 7.11 | 57 | 1.96 | 71 | 0.175 | 0.03 | 38.75 | 9153 | 8.36 | 58 |  | 177.03 | 3.25 | 6.85 | -3.882 | 0.16 | 79
8/24/2025 14:30 | -20 | 19 | 2.75 | 7.829 | 1.841 | 7.11 | 57 | 1.96 | 71 | 0.175 | 0.03 | 38.75 | 9153 | 8.36 | 58 |  | 177.55 | 3.27 | 6.85 | -3.882 | 0.18 | 82
8/24/2025 14:45 | -23 | 19 | 2.75 | 7.817 | 1.895 | 7.1 | 57 | 1.96 | 71 | 0.175 | 0.03 | 38.75 | 9153 | 8.35 | 58 |  | 177.75 | 3.27 | 6.84 | -3.882 | 0.16 | 74
8/24/2025 15:00 | -20 | 19 | 2.75 | 7.82 | 1.952 | 7.1 | 57 | 1.96 | 71 | 0.175 | 0.029 | 38.75 | 9153 | 8.33 | 58 |  | 177.75 | 3.27 | 6.85 | -3.882 | 0.21 | 76
8/24/2025 15:15 | -12 | 19 | 2.75 | 7.83 | 1.967 | 7.1 | 57 | 1.96 | 71 | 0.175 | 0.029 | 38.75 | 9153 | 8.32 | 58 |  | 177.48 | 3.26 | 6.85 | -3.882 | 0.16 | 90
8/24/2025 15:30 | -14 | 19 | 2.75 | 7.816 | 1.859 | 7.11 | 57 | 1.96 | 71 | 0.175 | 0.029 | 38.75 | 9153 | 8.32 | 58 |  | 176.69 | 3.26 | 6.85 | -3.882 | 0.18 | 86
8/24/2025 15:45 | -23 | 19 | 2.75 | 7.784 | 1.847 | 7.11 | 57 | 1.96 | 71 | 0.175 | 0.029 | 38.75 | 9153 | 8.3 | 58 |  | 177.24 | 3.28 | 6.85 | -3.882 | 0.18 | 74
8/24/2025 16:00 | -19 | 19 | 2.75 | 7.823 | 1.701 | 7.12 | 57 | 1.96 | 71 | 0.168 | 0.029 | 38.75 | 9153 | 8.3 | 58 |  | 176.99 | 3.26 | 6.85 | -3.882 | 0.17 | 78
8/24/2025 16:15 | -23 | 19 | 2.75 | 7.747 | 1.671 | 7.12 | 57 | 1.96 | 71 | 0.168 | 0.029 | 38.75 | 9153 | 8.28 | 58 |  | 0 | 0 | 6.85 | -3.882 | 0.17 | 73
8/24/2025 16:30 | -35 | 19 | 2.75 | 7.787 | 1.618 | 7.13 | 57 | 1.96 | 71 | 0.168 | 0.029 | 38.75 | 9153 | 8.28 | 58 |  | 181.15 | 3.35 | 6.86 | -3.882 | 0.17 | 71
8/24/2025 16:45 | -27 | 19 | 2.75 | 7.807 | 1.765 | 7.12 | 57 | 1.96 | 71 | 0.168 | 0.029 | 38.75 | 9153 | 8.27 | 58 |  | 180.86 | 3.34 | 6.85 | -3.882 | 0.18 | 68
8/24/2025 17:00 | -19 | 19 | 2.75 | 7.778 | 1.652 | 7.12 | 57 | 1.96 | 71 | 0.168 | 0.029 | 38.75 | 9153 | 8.27 | 58 |  | 180.51 | 3.34 | 6.84 | -3.882 | 0.15 | 79
8/24/2025 17:15 | -17 | 19 | 2.75 | 8.066 | 1.535 | 7.13 | 57 | 1.96 | 71 | 0.168 | 0.029 | 38.75 | 9153 | 8.26 | 58 |  | 180.82 | 3.23 | 6.86 | -3.882 | 0.15 | 81
8/24/2025 17:30 | -22 | 19 | 2.75 | 8.11 | 1.514 | 7.14 | 57 | 1.96 | 71 | 0.168 | 0.029 | 38.75 | 9153 | 8.26 | 58 |  | 180.59 | 3.21 | 6.87 | -3.882 | 0.16 | 75
8/24/2025 17:45 | -17 | 19 | 2.75 | 8.103 | 1.41 | 7.15 | 57 | 1.96 | 71 | 0.168 | 0.029 | 38.75 | 9153 | 8.26 | 58 |  | 180.37 | 3.21 | 6.87 | -3.882 | 0.22 | 80
8/24/2025 18:00 | -24 | 19 | 2.75 | 7.812 | 1.419 | 7.14 | 57 | 1.96 | 71.2 | 0.168 | 0.029 | 38.75 | 9153 | 8.25 | 58 |  | 180.45 | 3.33 | 6.85 | -3.882 | 0.16 | 73
8/24/2025 18:15 | -22 | 19 | 2.75 | 7.636 | 1.511 | 7.13 | 57 | 1.96 | 71.2 | 0.168 | 0.029 | 38.75 | 9153 | 8.24 | 58 |  | 180.5 | 3.4 | 6.84 | -3.882 | 0.17 | 76
8/24/2025 18:30 | -19 | 19 | 2.75 | 8.156 | 1.72 | 7.11 | 57 | 1.96 | 71.2 | 0.168 | 0.029 | 38.75 | 9153 | 8.24 | 58 |  | 180.4 | 3.19 | 6.8 | -3.882 | 0.3 | 79
8/24/2025 18:45 | -20 | 19 | 2.75 | 8.157 | 1.771 | 7.09 | 57 | 1.96 | 71.2 | 0.168 | 0.029 | 38.75 | 9153 | 8.24 | 58 |  | 180.45 | 3.19 | 6.78 | -3.882 | 0.33 | 78
8/24/2025 19:00 | -20 | 19 | 2.75 | 8.158 | 1.807 | 7.09 | 57 | 1.96 | 71.2 | 0.168 | 0.029 | 38.75 | 9153 | 8.27 | 58 |  | 180.44 | 3.19 | 6.79 | -3.882 | 0.22 | 79
8/24/2025 19:15 | -9 | 19 | 2.75 | 7.868 | 1.894 | 7.09 | 57 | 1.96 | 71.2 | 0.168 | 0.029 | 38.75 | 9153 | 8.29 | 58 |  | 180.75 | 3.31 | 6.8 | -3.882 | 0.2 | 101
8/24/2025 19:30 | -2 | 19 | 2.75 | 7.717 | 1.863 | 7.09 | 57 | 1.96 | 71.2 | 0.168 | 0.029 | 38.75 | 9153 | 8.3 | 58 |  | 181.05 | 3.38 | 6.82 | -3.882 | 0.2 | 101
8/24/2025 19:45 | -1 | 19 | 2.75 | 8.035 | 1.913 | 7.09 | 57 | 1.96 | 71.2 | 0.168 | 0.029 | 38.75 | 9153 | 8.31 | 58 |  | 180.59 | 3.24 | 6.83 | -3.882 | 0.21 | 101
8/24/2025 20:00 | -8 | 19 | 2.75 | 7.992 | 1.87 | 7.08 | 57 | 1.96 | 71.2 | 0.237 | 0.029 | 38.75 | 9153 | 8.3 | 58 |  | 180.19 | 3.25 | 6.82 | -3.882 | 0.22 | 101
8/24/2025 20:15 | -3 | 19 | 2.75 | 8.008 | 1.936 | 7.08 | 57 | 1.96 | 71.2 | 0.237 | 0.029 | 38.75 | 9153 | 8.3 | 58 |  | 180.74 | 3.25 | 6.81 | -3.882 | 0.21 | 101
8/24/2025 20:30 | -5 | 19 | 2.75 | 8.359 | 2.037 | 7.07 | 57 | 1.96 | 71.2 | 0.237 | 0.029 | 38.3 | 9095 | 8.31 | 58 |  | 180.48 | 3.11 | 6.81 | -3.882 | 0.24 | 101
8/24/2025 20:45 | -7 | 19 | 2.75 | 8.34 | 2.041 | 7.07 | 57 | 1.96 | 71.2 | 0.237 | 0.03 | 38.3 | 9095 | 8.31 | 58 |  | 180.4 | 3.11 | 6.81 | -3.882 | 0.21 | 101
8/24/2025 21:00 | -5 | 19 | 2.75 | 7.928 | 2.048 | 7.07 | 57 | 1.96 | 71.2 | 0.237 | 0.031 | 38.3 | 9095 | 8.31 | 58 |  | 180.24 | 3.27 | 6.83 | -3.882 | 0.21 | 101
8/24/2025 21:15 | -2 | 19 | 2.75 | 8.015 | 1.972 | 7.08 | 57 | 1.96 | 71.2 | 0.237 | 0.031 | 38.3 | 9095 | 8.31 | 58 |  | 180.24 | 3.24 | 6.83 | -3.882 | 0.19 | 101
8/24/2025 21:30 | -5 | 19 | 2.75 | 8.305 | 1.885 | 7.09 | 57 | 1.96 | 71.2 | 0.237 | 0.031 | 38.3 | 9095 | 8.29 | 58 |  | 180.34 | 3.13 | 6.83 | -3.882 | 0.21 | 101
8/24/2025 21:45 | -6 | 19 | 2.75 | 8.269 | 1.817 | 7.1 | 57 | 1.96 | 71.2 | 0.237 | 0.03 | 38.3 | 9095 | 8.27 | 58 |  | 180.01 | 3.13 | 6.84 | -3.882 | 0.21 | 101
8/24/2025 22:00 | 5 | 19 | 2.75 | 8.201 | 1.902 | 7.09 | 55 | 1.96 | 71 | 0.237 | 0.03 | 38.3 | 9095 | 8.29 | 58 |  | 179.55 | 3.15 | 6.84 | -3.882 | 0.21 | 101
8/24/2025 22:15 | -2 | 19 | 2.75 | 8.143 | 2.016 | 7.09 | 55 | 1.96 | 71 | 0.237 | 0.03 | 38.3 | 9095 | 8.32 | 58 |  | 179.94 | 3.18 | 6.83 | -3.882 | 0.19 | 101
8/24/2025 22:30 | -5 | 19 | 2.75 | 8.166 | 2.03 | 7.09 | 55 | 1.96 | 71 | 0.237 | 0.03 | 38.3 | 9095 | 8.33 | 58 |  | 180.3 | 3.18 | 6.83 | -3.882 | 0.2 | 101
8/24/2025 22:45 | -10 | 19 | 2.75 | 8.123 | 2.232 | 7.08 | 55 | 1.96 | 71 | 0.237 | 0.03 | 38.3 | 9095 | 8.33 | 58 |  | 179.95 | 3.19 | 6.81 | -3.882 | 0.2 | 93
8/24/2025 23:00 | -6 | 19 | 2.75 | 7.842 | 2.361 | 7.07 | 55 | 1.96 | 71 | 0.237 | 0.03 | 38.3 | 9095 | 8.31 | 58 |  | 179.89 | 3.3 | 6.82 | -3.882 | 0.22 | 101
8/24/2025 23:15 | -7 | 19 | 2.75 | 8.237 | 2.457 | 7.07 | 55 | 1.96 | 71 | 0.237 | 0.03 | 38.3 | 9095 | 8.3 | 58 |  | 179.58 | 3.14 | 6.82 | -3.882 | 0.18 | 101
8/24/2025 23:30 | -7 | 19 | 2.75 | 8.211 | 2.416 | 7.08 | 55 | 1.96 | 71 | 0.237 | 0.03 | 38.3 | 9095 | 8.3 | 58 |  | 179.67 | 3.15 | 6.82 | -3.882 | 0.19 | 101
8/24/2025 23:45 | -7 | 19 | 2.75 | 8.308 | 2.667 | 7.08 | 55 | 1.96 | 71 | 0.237 | 0.03 | 38.3 | 9095 | 8.29 | 58 |  | 180.02 | 3.12 | 6.81 | -3.882 | 0.21 | 101
8/25/2025 00:00 | -11 | 19 | 2.75 | 8.246 | 2.884 | 7.07 | 55 | 1.96 | 71 | 0.272 | 0.029 | 38.3 | 9095 | 8.28 | 58 | 1.51 | 179.69 | 3.14 | 6.81 | -3.882 | 0.18 | 89
8/25/2025 00:15 | -9 | 19 | 2.75 | 8.276 | 3.273 | 7.09 | 55 | 1.96 | 71 | 0.272 | 0.029 | 38.3 | 9095 | 8.27 | 58 | 1.51 | 0 | 0 | 6.82 | -3.882 | 0.19 | 93
8/25/2025 00:30 | -12 | 19 | 2.75 | 8.24 | 3.027 | 7.11 | 55 | 1.96 | 71 | 0.272 | 0.029 | 38.3 | 9095 | 8.26 | 58 | 1.51 | 0 | 0 | 6.82 | -3.882 | 0.19 | 89
8/25/2025 00:45 | -14 | 19 | 2.75 | 8.236 | 2.943 | 7.12 | 55 | 1.96 | 71 | 0.272 | 0.029 | 38.3 | 9095 | 8.26 | 58 | 1.51 | 0 | 0 | 6.81 | -3.882 | 0.23 | 87
8/25/2025 01:00 | -9 | 19 | 2.75 | 7.575 | 2.796 | 7.12 | 55 | 1.96 | 71 | 0.272 | 0.029 | 38.3 | 9095 | 8.26 | 58 | 1.51 | 0 | 0 | 6.82 | -3.882 | 0.19 | 93
8/25/2025 01:15 | -13 | 19 | 2.75 | 7.627 | 2.679 | 7.14 | 55 | 1.96 | 71 | 0.272 | 0.029 | 38.3 | 9095 | 8.26 | 58 | 1.51 | 177.99 | 3.36 | 6.85 | -3.882 | 0.21 | 84
8/25/2025 01:30 | -5 | 19 | 2.75 | 8.146 | 39.937 | 7.1 | 55 | 1.96 | 71 | 0.272 | 0.029 | 38.3 | 9095 | 8.28 | 58 | 1.51 | 178.28 | 3.15 | 6.86 | -3.882 | 0.25 | 101
8/25/2025 01:45 | -12 | 19 | 2.75 | 8.091 | 4.485 | 7.11 | 55 | 1.96 | 71 | 0.272 | 0.029 | 38.3 | 9095 | 8.29 | 58 | 1.51 | 178.29 | 3.17 | 6.85 | -3.882 | 0.28 | 89
8/25/2025 02:00 | -5 | 19 | 2.75 | 8.092 | 2.323 | 7.12 | 55 | 1.96 | 71 | 0.272 | 0.029 | 38.3 | 9095 | 8.29 | 57 | 1.51 | 178.46 | 3.18 | 6.87 | -3.882 | 0.2 | 101
8/25/2025 02:15 | -3 | 19 | 2.75 | 7.302 | 1.879 | 7.12 | 55 | 1.96 | 71 | 0.272 | 0.029 | 38.3 | 9095 | 8.29 | 57 | 1.51 | 177.15 | 3.49 | 6.88 | -3.882 | 0.2 | 101
8/25/2025 02:30 | -6 | 19 | 2.75 | 7.331 | 1.898 | 7.12 | 55 | 1.96 | 71 | 0.272 | 0.028 | 38.3 | 9095 | 8.29 | 57 | 1.51 | 177.58 | 3.49 | 6.88 | -3.882 | 0.22 | 101
8/25/2025 02:45 | -9 | 19 | 2.75 | 7.696 | 1.77 | 7.12 | 55 | 1.96 | 71 | 0.272 | 0.028 | 38.3 | 9095 | 8.29 | 57 | 1.51 | 177.61 | 3.32 | 6.87 | -3.882 | 0.2 | 94
8/25/2025 03:00 | -12 | 19 | 2.75 | 7.717 | 2.296 | 7.1 | 55 | 1.96 | 71 | 0.272 | 0.028 | 38.3 | 9095 | 8.29 | 57 | 1.51 | 176.98 | 3.3 | 6.83 | -3.882 | 0.18 | 90
8/25/2025 03:15 | -19 | 19 | 2.75 | 7.665 | 3.122 | 7.08 | 55 | 1.96 | 71 | 0.272 | 0.028 | 38.3 | 9095 | 8.29 | 57 | 1.51 | 176.85 | 3.32 | 6.81 | -3.882 | 0.17 | 76
8/25/2025 03:30 | -14 | 19 | 2.75 | 7.752 | 3.328 | 7.08 | 55 | 1.96 | 71 | 0.272 | 0.028 | 38.3 | 9095 | 8.29 | 57 | 1.51 | 176.6 | 3.28 | 6.8 | -3.882 | 0.19 | 87
8/25/2025 03:45 | -13 | 19 | 2.75 | 7.744 | 3.345 | 7.07 | 55 | 1.96 | 71 | 0.272 | 0.028 | 38.3 | 9095 | 8.28 | 57 | 1.51 | 177.26 | 3.3 | 6.81 | -3.882 | 0.16 | 88
8/25/2025 04:00 | -17 | 19 | 2.75 | 7.72 | 3.417 | 7.06 | 55 | 1.96 | 71 | 0.28 | 0.028 | 38.3 | 9095 | 8.28 | 57 | 1.51 | 176.89 | 3.3 | 6.81 | -3.882 | 0.17 | 81
8/25/2025 04:15 | -10 | 19 | 2.75 | 7.593 | 3.574 | 7.06 | 55 | 1.96 | 71 | 0.28 | 0.028 | 38.3 | 9095 | 8.29 | 57 | 1.51 | 177.16 | 3.36 | 6.81 | -3.882 | 0.17 | 93
8/25/2025 04:30 | -7 | 19 | 2.75 | 7.086 | 3.148 | 7.07 | 55 | 1.96 | 71 | 0.28 | 0.028 | 38.3 | 9095 | 8.3 | 57 | 1.51 | 172.97 | 3.52 | 6.84 | -3.882 | 0.16 | 101
8/25/2025 04:45 | -9 | 19 | 2.75 | 7.705 | 2.763 | 7.08 | 55 | 1.96 | 71 | 0.28 | 0.028 | 38.3 | 9095 | 8.31 | 57 | 1.51 | 177.4 | 3.32 | 6.86 | -3.882 | 0.17 | 101
8/25/2025 05:00 | -13 | 19 | 2.75 | 7.651 | 2.644 | 7.09 | 55 | 1.96 | 71 | 0.28 | 0.028 | 38.3 | 9095 | 8.33 | 57 | 1.51 | 176.94 | 3.33 | 6.85 | -3.882 | 0.18 | 91
8/25/2025 05:15 | -7 | 19 | 2.75 | 7.699 | 2.528 | 7.09 | 55 | 1.96 | 71 | 0.28 | 0.028 | 38.3 | 9095 | 8.34 | 57 | 1.51 | 176.34 | 3.3 | 6.85 | -3.882 | 0.16 | 101
8/25/2025 05:30 | -8 | 19 | 2.75 | 7.689 | 2.523 | 7.09 | 55 | 1.96 | 71 | 0.28 | 0.028 | 38.3 | 9095 | 8.34 | 57 | 1.51 | 169.38 | 3.17 | 6.84 | -3.882 | 0.18 | 101
8/25/2025 05:45 | -10 | 19 | 2.75 | 7.093 | 2.696 | 7.08 | 55 | 1.96 | 71 | 0.28 | 0.027 | 38.3 | 9095 | 8.35 | 57 | 1.51 | 147.11 | 2.99 | 6.85 | -3.882 | 0.21 | 93
8/25/2025 06:00 | -17 | 19 | 2.75 | 7.056 | 2.716 | 7.08 | 55 | 1.96 | 70.8 | 0.28 | 0.027 | 38.3 | 9095 | 8.35 | 57 | 1.51 | 146.99 | 3 | 6.86 | -3.882 | 0.19 | 83
8/25/2025 06:15 | -13 | 19 | 2.75 | 7.378 | 2.914 | 7.06 | 55 | 1.96 | 70.8 | 0.28 | 0.027 | 38.3 | 9095 | 8.36 | 57 | 1.51 | 154.25 | 3.01 | 6.83 | -3.882 | 0.17 | 86
8/25/2025 06:30 | -13 | 19 | 2.75 | 7.397 | 2.839 | 7.06 | 55 | 1.96 | 70.8 | 0.28 | 0.027 | 38.3 | 9095 | 8.36 | 57 | 1.51 | 154.55 | 3.01 | 6.82 | -3.882 | 0.16 | 90
8/25/2025 06:45 | -14 | 19 | 2.75 | 7.417 | 2.77 | 7.07 | 55 | 1.96 | 70.8 | 0.28 | 0.027 | 38.3 | 9095 | 8.37 | 57 | 1.51 | 154.45 | 3 | 6.82 | -3.882 | 0.18 | 86
8/25/2025 07:00 | -9 | 19 | 2.75 | 7.383 | 2.581 | 7.07 | 55 | 1.96 | 70.8 | 0.28 | 0.027 | 38.3 | 9095 | 8.37 | 57 | 1.51 | 154.02 | 3 | 6.83 | -3.882 | 0.19 | 101
8/25/2025 07:15 | -9 | 19 | 2.75 | 7.421 | 2.472 | 7.07 | 55 | 1.96 | 70.8 | 0.28 | 0.027 | 38.3 | 9095 | 8.37 | 57 | 1.51 | 154.08 | 2.99 | 6.83 | -3.882 | 0.17 | 93
8/25/2025 07:30 | -9 | 19 | 2.75 | 7.398 | 2.42 | 7.07 | 55 | 1.96 | 70.8 | 0.28 | 0.027 | 38.3 | 9095 | 8.38 | 57 | 1.51 | 153.69 | 2.99 | 6.84 | -3.882 | 0.17 | 101
8/25/2025 07:45 | -21 | 19 | 2.75 | 7.364 | 2.203 | 7.08 | 55 | 1.96 | 70.8 | 0.28 | 0.027 | 38.3 | 9095 | 8.38 | 57 | 1.51 | 153.83 | 3.01 | 6.83 | -3.882 | 0.25 | 84
8/25/2025 08:00 | -8 | 19 | 2.75 | 7.104 | 2.158 | 7.08 | 55 | 1.96 | 70.8 | 0.288 | 0.027 | 38.3 | 9095 | 8.38 | 57 | 1.51 | 147.16 | 2.98 | 6.83 | -3.882 | 0.16 | 95
8/25/2025 08:15 | -16 | 19 | 2.75 | 6.884 | 2.202 | 7.11 | 55 | 1.96 | 70.8 | 0.288 | 0.027 | 38.3 | 9095 | 8.38 | 57 | 1.51 | 0 | 0 | 6.86 | -3.882 | 0.19 | 83
8/25/2025 08:30 | -13 | 19 | 2.75 | 7.06 | 2.034 | 7.13 | 55 | 1.96 | 70.8 | 0.288 | 0.027 | 38.3 | 9095 | 8.38 | 57 | 1.51 | 0 | 0 | 6.86 | -3.882 | 0.19 | 89
8/25/2025 08:45 | -12 | 19 | 2.75 | 7.29 | 2.022 | 7.13 | 55 | 1.96 | 70.8 | 0.288 | 0.027 | 38.3 | 9095 | 8.39 | 57 | 1.51 | 0 | 0 | 6.85 | -3.882 | 0.19 | 89
8/25/2025 09:00 | -11 | 19 | 2.75 | 7.283 | 2.07 | 7.13 | 55 | 1.96 | 70.8 | 0.288 | 0.027 | 38.3 | 9095 | 8.39 | 57 | 1.51 | 0 | 0 | 6.84 | -3.882 | 0.18 | 93
8/25/2025 09:15 | -17 | 19 | 2.75 | 7.302 | 2.183 | 7.13 | 55 | 1.96 | 70.8 | 0.288 | 0.027 | 38.3 | 9095 | 8.38 | 57 | 1.51 | 0 | 0 | 6.83 | -3.882 | 0.16 | 101
8/25/2025 09:30 | -5 | 19 | 2.75 | 7.268 | 2.242 | 7.12 | 55 | 1.96 | 70.8 | 0.288 | 0.027 | 38.3 | 9095 | 8.39 | 57 | 1.51 | 0 | 0 | 6.84 | -3.882 | 0.16 | 101
8/25/2025 09:45 | -3 | 19 | 2.75 | 7.268 | 2.289 | 7.12 | 55 | 1.96 | 70.8 | 0.288 | 0.027 | 38.3 | 9095 | 8.39 | 57 | 1.51 | 0 | 0 | 6.84 | -3.882 | 0.17 | 101
8/25/2025 10:00 | 0 | 19 | 2.75 | 7.229 | 2.436 | 7.12 | 57 | 1.96 | 70.7 | 0.288 | 0.027 | 38.3 | 9095 | 8.38 | 57 | 1.51 | 0 | 0 | 6.84 | -3.882 | 0.19 | 101
8/25/2025 10:15 | 0 | 19 | 2.75 | 6.872 | 2.554 | 7.12 | 57 | 1.96 | 70.7 | 0.288 | 0.026 | 38.3 | 9095 | 8.38 | 57 | 1.51 | 0 | 0 | 6.84 | -3.882 | 0.18 | 101
8/25/2025 10:30 | -3 | 19 | 2.75 | 7.073 | 2.613 | 7.12 | 57 | 1.96 | 70.7 | 0.288 | 0.026 | 38.3 | 9095 | 8.39 | 57 | 1.51 | 0 | 0 | 6.84 | -3.882 | 0.17 | 101
8/25/2025 10:45 | 0 | 19 | 2.75 | 7.077 | 2.585 | 7.11 | 57 | 1.96 | 70.7 | 0.288 | 0.026 | 38.3 | 9095 | 8.39 | 57 | 1.51 | 0 | 0 | 6.84 | -3.882 | 0.17 | 101
8/25/2025 11:00 | 0 | 19 | 2.75 | 7.095 | 2.505 | 7.11 | 57 | 1.96 | 70.7 | 0.288 | 0.026 | 38.3 | 9095 | 8.4 | 57 | 1.51 | 0 | 0 | 6.85 | -3.882 | 0.15 | 101
8/25/2025 11:15 | -2 | 19 | 2.75 | 7.096 | 2.393 | 7.12 | 57 | 1.96 | 70.7 | 0.288 | 0.026 | 38.3 | 9095 | 8.41 | 57 | 1.51 | 0 | 0 | 6.85 | -3.882 | 0.16 | 101
8/25/2025 11:30 | -1 | 19 | 2.75 | 7.075 | 2.314 | 7.13 | 57 | 1.96 | 70.7 | 0.288 | 0.027 | 38.3 | 9095 | 8.41 | 57 | 1.51 | 0 | 0 | 6.86 | -3.882 | 0.17 | 101
8/25/2025 11:45 | -2 | 19 | 2.75 | 7.057 | 2.314 | 7.13 | 57 | 1.96 | 70.7 | 0.288 | 0.027 | 38.51 | 9118 | 8.42 | 57 | 1.51 | 0 | 0 | 6.86 | -3.882 | 0.14 | 101
8/25/2025 12:00 | -1 | 19 | 2.75 | 7.061 | 2.281 | 7.13 | 57 | 1.96 | 70.7 | 0.183 | 0.028 | 38.51 | 9118 | 8.42 | 57 | 1.51 | 0 | 0 | 6.81 | -3.823 | 0.15 | 101
8/25/2025 12:15 | 0 | 19 | 2.75 | 7.042 | 2.304 | 7.13 | 57 | 1.96 | 70.7 | 0.183 | 0.029 | 38.51 | 9118 | 8.41 | 57 | 1.51 | 0 | 0 | 6.81 | -3.823 | 0.18 | 101
8/25/2025 12:30 | -2 | 19 | 2.75 | 7.041 | 2.243 | 7.13 | 57 | 1.96 | 70.7 | 0.183 | 0.029 | 38.51 | 9118 | 8.41 | 57 | 1.51 | 0 | 0 | 6.87 | -3.823 | 0.18 | 101
8/25/2025 12:45 | -1 | 19 | 2.75 | 7.065 | 2.233 | 7.13 | 57 | 1.96 | 70.7 | 0.183 | 0.029 | 38.51 | 9118 | 8.4 | 57 | 1.51 | 0 | 0 | 6.88 | -3.823 | 0.17 | 101
8/25/2025 13:00 | -1 | 19 | 2.75 | 7.069 | 2.149 | 7.14 | 57 | 1.96 | 70.7 | 0.183 | 0.029 | 38.51 | 9118 | 8.38 | 57 | 1.51 | 0 | 0 | 6.88 | -3.823 | 0.18 | 101
8/25/2025 13:15 | 0 | 19 | 2.75 | 7.1 | 2.125 | 7.15 | 57 | 1.96 | 70.7 | 0.183 | 0.029 | 38.51 | 9118 | 8.37 | 57 | 1.51 | 0 | 0 | 6.88 | -3.823 | 0.16 | 101
8/25/2025 13:30 | -3 | 19 | 2.75 | 7.09 | 2.09 | 7.15 | 57 | 1.96 | 70.7 | 0.183 | 0.029 | 38.51 | 9118 | 8.39 | 57 | 1.51 | 0 | 0 | 6.87 | -3.823 | 0.16 | 101
8/25/2025 13:45 | -3 | 19 | 2.75 | 7.032 | 2.132 | 7.15 | 57 | 1.96 | 70.7 | 0.183 | 0.029 | 38.51 | 9118 | 8.42 | 57 | 1.51 | 0 | 0 | 6.86 | -3.823 | 0.14 | 101
8/25/2025 14:00 | 0 | 19 | 2.75 | 6.625 | 2.083 | 7.15 | 57 | 1.96 | 70.8 | 0.183 | 0.029 | 38.51 | 9118 | 8.45 | 58 | 1.51 | 0 | 0 | 6.86 | -3.823 | 0.22 | 101
8/25/2025 14:15 | 0 | 19 | 2.75 | 6.71 | 2.028 | 7.15 | 57 | 1.96 | 70.8 | 0.183 | 0.029 | 38.51 | 9118 | 8.46 | 58 | 1.51 | 0 | 0 | 6.86 | -3.823 | 0.16 | 101
8/25/2025 14:30 | -1 | 19 | 2.75 | 6.955 | 1.954 | 7.15 | 57 | 1.96 | 70.8 | 0.183 | 0.029 | 38.51 | 9118 | 8.47 | 58 | 1.51 | 0 | 0 | 6.86 | -3.823 | 0.17 | 101
8/25/2025 14:45 | -2 | 19 | 2.75 | 6.957 | 1.843 | 7.16 | 57 | 1.96 | 70.8 | 0.183 | 0.029 | 38.51 | 9118 | 8.47 | 58 | 1.51 | 0 | 0 | 6.87 | -3.823 | 0.2 | 101
8/25/2025 15:00 | 0 | 19 | 2.75 | 6.936 | 1.851 | 7.17 | 57 | 1.96 | 70.8 | 0.183 | 0.029 | 38.51 | 9118 | 8.46 | 58 | 1.51 | 0 | 0 | 6.87 | -3.823 | 0.16 | 101
8/25/2025 15:15 | 0 | 19 | 2.75 | 6.944 | 2.204 | 7.16 | 57 | 1.96 | 70.8 | 0.183 | 0.029 | 38.51 | 9118 | 8.46 | 58 | 1.51 | 0 | 0 | 6.85 | -3.823 | 0.15 | 101
8/25/2025 15:30 | -1 | 19 | 2.75 | 6.952 | 2.083 | 7.16 | 57 | 1.96 | 70.8 | 0.183 | 0.029 | 38.51 | 9118 | 8.46 | 58 | 1.51 | 0 | 0 | 6.84 | -3.823 | 0.16 | 101
8/25/2025 15:45 | -3 | 19 | 2.75 | 6.921 | 2.085 | 7.17 | 57 | 1.96 | 70.8 | 0.183 | 0.029 | 38.51 | 9118 | 8.46 | 58 | 1.51 | 0 | 0 | 6.84 | -3.823 | 0.15 | 101
8/25/2025 16:00 | -2 | 19 | 2.75 | 6.94 | 2.077 | 7.16 | 57 | 1.96 | 70.8 | 0.186 | 0.029 | 38.51 | 9118 | 8.45 | 58 | 1.51 | 144.5 | 3 | 6.84 | -3.823 | 0.14 | 101
8/25/2025 16:15 | -4 | 19 | 2.75 | 6.956 | 2.037 | 7.13 | 57 | 1.96 | 70.8 | 0.186 | 0.029 | 38.51 | 9118 | 8.45 | 58 | 1.51 | 144.76 | 3 | 6.83 | -3.823 | 0.15 | 101
8/25/2025 16:30 | -2 | 19 | 2.75 | 6.94 | 1.993 | 7.12 | 57 | 1.96 | 70.8 | 0.186 | 0.029 | 38.51 | 9118 | 8.45 | 58 | 1.51 | 144.78 | 3 | 6.83 | -3.823 | 0.16 | 101
8/25/2025 16:45 | 0 | 19 | 2.75 | 5.868 | 2.146 | 7.12 | 57 | 1.96 | 70.8 | 0.186 | 0.029 | 38.51 | 9118 | 8.45 | 58 | 1.51 | 122.05 | 3 | 6.81 | -3.823 | 0.13 | 101
8/25/2025 17:00 | 1 | 19 | 2.75 | 5.514 | 2.198 | 7.11 | 57 | 1.96 | 70.8 | 0.186 | 0.029 | 38.34 | 9080 | 8.46 | 58 | 1.51 | 114.96 | 3 | 6.79 | -3.823 | 0.15 | 101
8/25/2025 17:15 | 1 | 19 | 2.75 | 5.847 | 2.204 | 7.1 | 57 | 1.96 | 70.8 | 0.186 | 0.029 | 38.34 | 9080 | 8.46 | 58 | 1.51 | 121.43 | 2.99 | 6.79 | -3.823 | 0.17 | 101
8/25/2025 17:30 | -1 | 19 | 2.75 | 5.857 | 2.227 | 7.1 | 57 | 1.96 | 70.8 | 0.186 | 0.029 | 38.34 | 9080 | 8.46 | 58 | 1.51 | 121.48 | 2.99 | 6.8 | -3.823 | 0.14 | 101
8/25/2025 17:45 | 1 | 19 | 2.75 | 5.833 | 2.344 | 7.09 | 57 | 1.96 | 70.8 | 0.186 | 0.029 | 38.34 | 9080 | 8.46 | 58 | 1.51 | 121.68 | 3 | 6.81 | -3.823 | 0.26 | 101
8/25/2025 18:00 | 1 | 19 | 2.75 | 5.839 | 2.463 | 7.09 | 57 | 1.96 | 70.7 | 0.186 | 0.029 | 38.34 | 9080 | 8.46 | 58 | 1.51 | 121.49 | 3 | 6.82 | -3.823 | 0.16 | 101
8/25/2025 18:15 | 2 | 19 | 2.75 | 5.816 | 2.389 | 7.09 | 57 | 1.96 | 70.7 | 0.186 | 0.029 | 38.34 | 9080 | 8.46 | 58 | 1.51 | 121.58 | 3.01 | 6.82 | -3.823 | 0.12 | 101
8/25/2025 18:30 | 0 | 19 | 2.75 | 5.84 | 2.389 | 7.09 | 57 | 1.96 | 70.7 | 0.186 | 0.029 | 38.34 | 9080 | 8.44 | 58 | 1.51 | 121.94 | 3.01 | 6.83 | -3.823 | 0.14 | 101
8/25/2025 18:45 | 3 | 19 | 2.75 | 5.831 | 2.431 | 7.08 | 57 | 1.96 | 70.7 | 0.186 | 0.029 | 38.34 | 9080 | 8.41 | 58 | 1.51 | 121.74 | 3.01 | 6.83 | -3.823 | 0.14 | 101
8/25/2025 19:00 | 3 | 19 | 2.75 | 5.849 | 2.441 | 7.08 | 57 | 1.96 | 70.7 | 0.186 | 0.029 | 38.34 | 9080 | 8.4 | 58 | 1.51 | 121.05 | 2.98 | 6.83 | -3.823 | 0.13 | 101
8/25/2025 19:15 | 4 | 19 | 2.75 | 5.851 | 2.375 | 7.08 | 57 | 1.96 | 70.7 | 0.186 | 0.029 | 38.34 | 9080 | 8.41 | 58 | 1.51 | 121.27 | 2.98 | 6.83 | -3.823 | 0.14 | 101
8/25/2025 19:30 | 5 | 19 | 2.75 | 5.841 | 2.178 | 7.09 | 57 | 1.96 | 70.7 | 0.186 | 0.029 | 38.34 | 9080 | 8.42 | 58 | 1.51 | 121.7 | 3 | 6.84 | -3.823 | 0.15 | 101
8/25/2025 19:45 | 3 | 19 | 2.75 | 5.85 | 2.11 | 7.1 | 57 | 1.96 | 70.7 | 0.186 | 0.029 | 38.34 | 9080 | 8.44 | 58 | 1.51 | 122.03 | 3 | 6.85 | -3.823 | 0.18 | 101
8/25/2025 20:00 | 5 | 19 | 2.75 | 5.86 | 2.114 | 7.1 | 57 | 1.96 | 70.7 | 0.176 | 0.029 | 38.34 | 9080 | 8.45 | 58 | 1.51 | 121.65 | 2.99 | 6.85 | -3.823 | 0.23 | 101
8/25/2025 20:15 | 2 | 19 | 2.75 | 5.892 | 2.096 | 7.09 | 57 | 1.96 | 70.7 | 0.176 | 0.029 | 38.34 | 9080 | 8.46 | 58 | 1.51 | 143.91 | 3.52 | 6.85 | -3.823 | 0.19 | 101
8/25/2025 20:30 | 2 | 19 | 2.75 | 5.808 | 2.224 | 7.09 | 57 | 1.96 | 70.7 | 0.176 | 0.029 | 38.34 | 9080 | 8.46 | 58 | 1.51 | 160.91 | 3.99 | 6.84 | -3.823 | 0.13 | 101
8/25/2025 20:45 | 0 | 19 | 2.75 | 5.05 | 2.231 | 7.09 | 57 | 1.96 | 70.7 | 0.176 | 0.029 | 38.34 | 9080 | 8.47 | 58 | 1.51 | 140 | 3.99 | 6.84 | -3.823 | 0.13 | 101
8/25/2025 21:00 | 3 | 19 | 2.75 | 5.061 | 2.26 | 7.08 | 57 | 1.96 | 70.7 | 0.176 | 0.029 | 38.34 | 9080 | 8.47 | 58 | 1.51 | 140.77 | 4.01 | 6.87 | -3.823 | 0.13 | 101
8/25/2025 21:15 | 2 | 19 | 2.75 | 5.435 | 2.267 | 7.09 | 57 | 1.96 | 70.7 | 0.176 | 0.029 | 38.34 | 9080 | 8.47 | 58 | 1.51 | 150.42 | 3.99 | 6.85 | -3.823 | 0.13 | 101
8/25/2025 21:30 | 2 | 19 | 2.75 | 5.448 | 2.253 | 7.08 | 57 | 1.96 | 70.7 | 0.176 | 0.029 | 38.34 | 9080 | 8.47 | 58 | 1.51 | 150.63 | 3.98 | 6.83 | -3.823 | 0.19 | 101
8/25/2025 21:45 | 0 | 19 | 2.75 | 5.432 | 2.209 | 7.09 | 57 | 1.96 | 70.7 | 0.176 | 0.029 | 38.34 | 9080 | 8.47 | 58 | 1.51 | 151.05 | 4 | 6.83 | -3.823 | 0.2 | 101
8/25/2025 22:00 | 1 | 19 | 2.75 | 5.448 | 2.15 | 7.09 | 58 | 1.96 | 70.3 | 0.176 | 0.029 | 38.34 | 9080 | 8.47 | 58 | 1.51 | 0 | 0 | 6.84 | -3.823 | 0.14 | 101
8/25/2025 22:15 | 1 | 19 | 2.75 | 5.446 | 2.331 | 7.1 | 58 | 1.96 | 70.3 | 0.176 | 0.029 | 38.34 | 9080 | 8.47 | 58 | 1.51 | 151.51 | 4.01 | 6.84 | -3.823 | 0.15 | 101
8/25/2025 22:30 | 3 | 19 | 2.75 | 6.131 | 39.937 | 7.06 | 58 | 1.96 | 70.3 | 0.176 | 0.029 | 38.05 | 9042 | 8.47 | 58 | 1.51 | 168.28 | 3.95 | 6.82 | -3.823 | 0.26 | 101
8/25/2025 22:45 | 0 | 19 | 2.75 | 6.498 | 4.325 | 7.05 | 58 | 1.96 | 70.3 | 0.176 | 0.029 | 38.05 | 9042 | 8.47 | 58 | 1.51 | 178.12 | 3.95 | 6.81 | -3.823 | 0.17 | 101
8/25/2025 23:00 | 4 | 19 | 2.75 | 4.997 | 3.367 | 7.04 | 58 | 1.96 | 70.3 | 0.176 | 0.03 | 38.05 | 9042 | 8.47 | 58 | 1.51 | 139.74 | 4.03 | 6.81 | -3.823 | 0.15 | 101
8/25/2025 23:15 | 4 | 19 | 2.75 | 5.075 | 2.735 | 7.03 | 58 | 1.96 | 70.3 | 0.176 | 0.031 | 38.05 | 9042 | 8.47 | 58 | 1.51 | 139.95 | 3.97 | 6.82 | -3.823 | 0.17 | 101
8/25/2025 23:30 | 3 | 19 | 2.75 | 5.523 | 2.717 | 7.03 | 58 | 1.96 | 70.3 | 0.176 | 0.032 | 38.05 | 9042 | 8.47 | 58 | 1.51 | 152.7 | 3.98 | 6.81 | -3.823 | 0.16 | 101
8/25/2025 23:45 | 0 | 19 | 2.75 | 5.517 | 2.719 | 7.02 | 58 | 1.96 | 70.3 | 0.176 | 0.032 | 38.05 | 9042 | 8.48 | 58 | 1.51 | 153.61 | 4.01 | 6.8 | -3.823 | 0.2 | 101
8/26/2025 00:00 | 3 | 19 | 2.75 | 5.519 | 2.728 | 7.01 | 58 | 2 | 70.3 | 0.2 | 0.031 | 38.05 | 9042 | 8.48 | 58 |  | 153.15 | 4 | 6.8 | -3.823 | 0.16 | 101
8/26/2025 00:15 | 3 | 19 | 2.75 | 5.501 | 2.813 | 7.01 | 58 | 2 | 70.3 | 0.2 | 0.031 | 38.05 | 9042 | 8.48 | 58 |  | 152.96 | 4 | 6.8 | -3.823 | 0.17 | 101
8/26/2025 00:30 | 2 | 19 | 2.75 | 5.524 | 3.009 | 7 | 58 | 2 | 70.3 | 0.2 | 0.031 | 38.05 | 9042 | 8.49 | 58 |  | 152.85 | 3.98 | 6.81 | -3.823 | 0.17 | 101
8/26/2025 00:45 | 3 | 19 | 2.75 | 5.494 | 3.023 | 7 | 58 | 2 | 70.3 | 0.2 | 0.031 | 38.05 | 9042 | 8.51 | 58 |  | 153.28 | 4.02 | 6.81 | -3.823 | 0.18 | 101
8/26/2025 01:00 | 2 | 19 | 2.75 | 5.509 | 3.191 | 7 | 58 | 2 | 70.3 | 0.2 | 0.031 | 38.05 | 9042 | 8.54 | 58 |  | 152.8 | 3.99 | 6.81 | -3.823 | 0.16 | 101
8/26/2025 01:15 | 2 | 19 | 2.75 | 5.5 | 3.27 | 7 | 58 | 2 | 70.3 | 0.2 | 0.03 | 38.05 | 9042 | 8.56 | 58 |  | 152.97 | 4.01 | 6.81 | -3.823 | 0.21 | 101
8/26/2025 01:30 | 1 | 19 | 2.75 | 5.513 | 3.238 | 7 | 58 | 2 | 70.3 | 0.2 | 0.03 | 38.05 | 9042 | 8.56 | 58 |  | 152.7 | 3.99 | 6.81 | -3.823 | 0.21 | 101
8/26/2025 01:45 | 0 | 19 | 2.75 | 5.502 | 3.199 | 7 | 58 | 2 | 70.3 | 0.2 | 0.03 | 38.05 | 9042 | 8.56 | 58 |  | 152.58 | 3.99 | 6.81 | -3.823 | 0.17 | 101
8/26/2025 02:00 | 1 | 19 | 2.75 | 5.507 | 37.258 | 6.74 | 58 | 2 | 70.3 | 0.2 | 0.03 | 38.05 | 9042 | 8.55 | 59 |  | 152.97 | 4 | 6.81 | -3.823 | 0.15 | 101
8/26/2025 02:15 | 2 | 19 | 2.75 | 5.51 | 4.953 | 6.92 | 58 | 2 | 70.3 | 0.2 | 0.03 | 38.05 | 9042 | 8.55 | 59 |  | 152.96 | 4 | 6.82 | -3.823 | 0.14 | 101
8/26/2025 02:30 | 2 | 19 | 2.75 | 5.401 | 2.081 | 6.98 | 58 | 2 | 70.3 | 0.2 | 0.03 | 38.05 | 9042 | 8.54 | 59 |  | 150.68 | 4.02 | 6.83 | -3.823 | 0.15 | 101
8/26/2025 02:45 | 2 | 19 | 2.75 | 5.082 | 1.835 | 7.06 | 58 | 2 | 70.3 | 0.2 | 0.03 | 38.05 | 9042 | 8.53 | 59 |  | 141.17 | 4 | 6.84 | -3.823 | 0.15 | 101
8/26/2025 03:00 | 3 | 19 | 2.75 | 5.327 | 1.751 | 7.06 | 58 | 2 | 70.3 | 0.2 | 0.03 | 38.05 | 9042 | 8.52 | 59 |  | 177.03 | 4.79 | 6.84 | -3.823 | 0.17 | 101
8/26/2025 03:15 | 3 | 19 | 2.75 | 5.331 | 1.728 | 7.06 | 58 | 2 | 70.3 | 0.2 | 0.03 | 38.05 | 9042 | 8.51 | 59 |  | 176.86 | 4.78 | 6.83 | -3.823 | 0.15 | 101
8/26/2025 03:30 | 2 | 19 | 2.75 | 5.334 | 1.851 | 7.06 | 58 | 2 | 70.3 | 0.2 | 0.03 | 38.05 | 9042 | 8.5 | 59 |  | 177.47 | 4.79 | 6.82 | -3.823 | 0.14 | 101
8/26/2025 03:45 | 3 | 19 | 2.75 | 5.326 | 1.771 | 7.06 | 58 | 2 | 70.3 | 0.2 | 0.03 | 38.05 | 9042 | 8.48 | 59 |  | 176.6 | 4.77 | 6.82 | -3.823 | 0.13 | 101
8/26/2025 04:00 | 3 | 19 | 2.75 | 5.49 | 1.764 | 7.06 | 58 | 2 | 70.3 | 0.226 | 0.03 | 38.05 | 9042 | 8.47 | 59 |  | 176.85 | 4.64 | 6.83 | -3.823 | 0.23 | 101
8/26/2025 04:15 | 3 | 19 | 2.75 | 5.595 | 1.68 | 7.06 | 58 | 2 | 70.3 | 0.226 | 0.03 | 39.02 | 9098 | 8.46 | 59 |  | 177.21 | 4.56 | 6.83 | -3.823 | 0.14 | 101
8/26/2025 04:30 | 0 | 19 | 2.75 | 5.593 | 1.624 | 7.06 | 58 | 2 | 70.3 | 0.226 | 0.03 | 39.02 | 9098 | 8.45 | 59 |  | 176.38 | 4.54 | 6.83 | -3.823 | 0.13 | 101
8/26/2025 04:45 | 5 | 19 | 2.75 | 5.562 | 1.558 | 7.06 | 58 | 2 | 70.3 | 0.226 | 0.031 | 39.02 | 9098 | 8.44 | 59 |  | 176.87 | 4.58 | 6.83 | -3.823 | 0.15 | 101
8/26/2025 05:00 | 2 | 19 | 2.75 | 5.575 | 1.541 | 7.06 | 58 | 2 | 70.3 | 0.226 | 0.032 | 39.02 | 9098 | 8.43 | 59 |  | 176.56 | 4.56 | 6.83 | -3.823 | 0.14 | 101
8/26/2025 05:15 | 4 | 19 | 2.75 | 5.563 | 1.54 | 7.06 | 58 | 2 | 70.3 | 0.226 | 0.032 | 39.02 | 9098 | 8.43 | 59 |  | 176.51 | 4.57 | 6.83 | -3.823 | 0.15 | 101
8/26/2025 05:30 | 0 | 19 | 2.75 | 5.598 | 1.499 | 7.06 | 58 | 2 | 70.3 | 0.226 | 0.032 | 39.02 | 9098 | 8.42 | 59 |  | 176.5 | 4.54 | 6.84 | -3.823 | 0.13 | 101
8/26/2025 05:45 | 4 | 19 | 2.75 | 5.93 | 1.548 | 7.06 | 58 | 2 | 70.3 | 0.226 | 0.032 | 39.02 | 9098 | 8.4 | 59 |  | 176.76 | 4.29 | 6.83 | -3.823 | 0.16 | 101
8/26/2025 06:00 | 2 | 19 | 2.75 | 5.617 | 1.523 | 7.06 | 58 | 2 | 70.1 | 0.226 | 0.032 | 38.19 | 8975 | 8.37 | 59 |  | 176.08 | 4.51 | 6.83 | -3.823 | 0.14 | 101
8/26/2025 06:15 | 3 | 19 | 2.75 | 5.161 | 1.597 | 7.06 | 58 | 2 | 70.1 | 0.226 | 0.033 | 38.19 | 8975 | 8.36 | 59 |  | 176.41 | 4.92 | 6.84 | -3.823 | 0.38 | 101
8/26/2025 06:30 | 3 | 19 | 2.75 | 5.441 | 1.624 | 7.06 | 58 | 2 | 70.1 | 0.226 | 0.033 | 38.19 | 8975 | 8.37 | 59 |  | 187.89 | 4.97 | 6.86 | -3.823 | 0.21 | 101
8/26/2025 06:45 | 1 | 19 | 2.75 | 5.751 | 1.818 | 7.07 | 58 | 2 | 70.1 | 0.226 | 0.034 | 38.19 | 8975 | 8.38 | 59 |  | 158.57 | 3.97 | 6.84 | -3.823 | 0.16 | 101
8/26/2025 07:00 | 1 | 19 | 2.75 | 5.702 | 2.149 | 7.08 | 58 | 2 | 70.1 | 0.226 | 0.034 | 38.19 | 8975 | 8.4 | 59 |  | 158.83 | 4.01 | 6.83 | -3.823 | 0.2 | 101
8/26/2025 07:15 | 1 | 19 | 2.75 | 5.701 | 1.919 | 7.09 | 58 | 2 | 70.1 | 0.226 | 0.034 | 38.19 | 8975 | 8.4 | 59 |  | 158.5 | 4 | 6.87 | -3.823 | 0.13 | 101
8/26/2025 07:30 | -5 | 19 | 2.75 | 5.029 | 2.013 | 7.06 | 58 | 2 | 70.1 | 0.226 | 0.034 | 38.19 | 8975 | 8.39 | 59 |  | 140.63 | 4.03 | 6.79 | -3.823 | 0.23 | 101
8/26/2025 07:45 | 0 | 19 | 2.75 | 5.469 | 2.194 | 7.06 | 58 | 2 | 70.1 | 0.226 | 0.033 | 38.19 | 8975 | 8.39 | 59 |  | 149.5 | 3.94 | 6.79 | -3.823 | 0.2 | 101
8/26/2025 08:00 | 0 | 19 | 2.75 | 5.647 | 1.772 | 7.08 | 58 | 2 | 70.1 | 0.228 | 0.033 | 38.19 | 8975 | 8.39 | 59 |  | 160.12 | 4.08 | 6.82 | -3.823 | 0.2 | 101
8/26/2025 08:15 | 0 | 19 | 2.75 | 6.066 | 1.788 | 7.09 | 58 | 2 | 70.1 | 0.228 | 0.033 | 38.19 | 8975 | 8.41 | 59 |  | 166.66 | 3.96 | 6.84 | -3.823 | 0.2 | 101
8/26/2025 08:30 | 1 | 19 | 2.75 | 6.614 | 1.764 | 7.09 | 58 | 2 | 70.1 | 0.228 | 0.033 | 38.19 | 8975 | 8.43 | 59 |  | 179.97 | 3.92 | 6.87 | -3.823 | 0.21 | 101
8/26/2025 08:45 | 0 | 19 | 2.75 | 6.601 | 1.854 | 7.09 | 58 | 2 | 70.1 | 0.228 | 0.033 | 38.19 | 8975 | 8.45 | 59 |  | 179.54 | 3.92 | 6.86 | -3.823 | 0.21 | 101
8/26/2025 09:00 | 0 | 19 | 2.75 | 6.289 | 1.975 | 7.09 | 58 | 2 | 70.1 | 0.228 | 0.033 | 38.19 | 8975 | 8.45 | 59 |  | 175.08 | 4.01 | 6.84 | -3.823 | 0.23 | 101
8/26/2025 09:15 | 4 | 19 | 2.75 | 6.182 | 2.117 | 7.08 | 58 | 2 | 70.1 | 0.228 | 0.033 | 38.19 | 8975 | 8.45 | 59 |  | 169.05 | 3.94 | 6.83 | -3.823 | 0.2 | 101
8/26/2025 09:30 | 3 | 19 | 2.75 | 6.416 | 2.165 | 7.09 | 58 | 2 | 70.1 | 0.228 | 0.033 | 38.19 | 8975 | 8.45 | 59 |  | 178.38 | 4 | 6.83 | -3.823 | 0.2 | 101
8/26/2025 09:45 | 3 | 19 | 2.75 | 6.395 | 2.231 | 7.09 | 58 | 2 | 70.1 | 0.228 | 0.033 | 38.19 | 8975 | 8.43 | 59 |  | 177.83 | 4 | 6.83 | -3.823 | 0.21 | 101
8/26/2025 10:00 | 1 | 19 | 2.75 | 6.385 | 2.265 | 7.09 | 53 | 2 | 70.1 | 0.228 | 0.033 | 38.19 | 8975 | 8.42 | 59 |  | 178.15 | 4.02 | 6.83 | -3.823 | 0.21 | 101
8/26/2025 10:15 | 2 | 19 | 2.75 | 6.401 | 2.261 | 7.1 | 53 | 2 | 70.1 | 0.228 | 0.033 | 38.19 | 8975 | 8.41 | 59 |  | 178.01 | 4 | 6.83 | -3.823 | 0.21 | 101
8/26/2025 10:30 | 0 | 19 | 2.75 | 6.641 | 2.234 | 7.1 | 53 | 2 | 70.1 | 0.228 | 0.033 | 38.19 | 8975 | 8.41 | 59 |  | 180.06 | 3.9 | 6.83 | -3.823 | 0.21 | 101
8/26/2025 10:45 | 2 | 19 | 2.75 | 6.574 | 2.153 | 7.11 | 53 | 2 | 70.1 | 0.228 | 0.033 | 38.19 | 8975 | 8.41 | 59 |  | 179.72 | 3.94 | 6.83 | -3.823 | 0.21 | 101
8/26/2025 11:00 | 3 | 19 | 2.75 | 5.945 | 2.179 | 7.11 | 53 | 2 | 70.1 | 0.228 | 0.033 | 38.19 | 8975 | 8.41 | 59 |  | 164.57 | 3.99 | 6.83 | -3.823 | 0.23 | 101
8/26/2025 11:15 | 1 | 19 | 2.75 | 5.923 | 2.202 | 7.11 | 53 | 2 | 70.1 | 0.228 | 0.032 | 38.19 | 8975 | 8.41 | 59 |  | 165.04 | 4.01 | 6.82 | -3.823 | 0.2 | 101
8/26/2025 11:30 | 2 | 19 | 2.75 | 6.688 | 2.238 | 7.11 | 53 | 2 | 70.1 | 0.228 | 0.032 | 38.19 | 8975 | 8.41 | 59 |  | 179.99 | 3.88 | 6.84 | -3.823 | 0.24 | 101
8/26/2025 11:45 | 2 | 19 | 2.75 | 6.858 | 2.253 | 7.11 | 53 | 2 | 70.1 | 0.228 | 0.032 | 38.19 | 8975 | 8.4 | 59 |  | 180.46 | 3.79 | 6.84 | -3.823 | 0.21 | 101
8/26/2025 12:00 | 3 | 19 | 2.75 | 6.755 | 2.187 | 7.12 | 53 | 2 | 70.1 | 0.164 | 0.032 | 38.19 | 8975 | 8.4 | 59 |  | 179.65 | 3.83 | 6.85 | -3.72 | 0.21 | 101
8/26/2025 12:15 | 3 | 19 | 2.75 | 6.054 | 2.164 | 7.12 | 53 | 2 | 70.1 | 0.164 | 0.032 | 38.19 | 8975 | 8.4 | 59 |  | 169.38 | 4.03 | 6.86 | -3.72 | 0.21 | 101
8/26/2025 12:30 | 5 | 19 | 2.75 | 5.734 | 2.087 | 7.12 | 53 | 2 | 70.1 | 0.164 | 0.032 | 38.19 | 8975 | 8.4 | 59 |  | 161.01 | 4.04 | 6.86 | -3.72 | 0.21 | 101
8/26/2025 12:45 | 5 | 19 | 2.75 | 6.071 | 1.954 | 7.12 | 53 | 2 | 70.1 | 0.164 | 0.032 | 38.19 | 8975 | 8.4 | 59 |  | 169.58 | 4.02 | 6.86 | -3.72 | 0.21 | 101
8/26/2025 13:00 | 4 | 19 | 2.75 | 6.052 | 1.873 | 7.13 | 53 | 2 | 70.1 | 0.164 | 0.032 | 38.19 | 8975 | 8.4 | 59 |  | 168.45 | 4.01 | 6.86 | -3.72 | 0.22 | 101
8/26/2025 13:15 | 3 | 19 | 2.75 | 6.096 | 1.788 | 7.13 | 53 | 2 | 70.1 | 0.164 | 0.032 | 38.19 | 8975 | 8.38 | 59 |  | 169.53 | 4 | 6.85 | -3.72 | 0.21 | 101
8/26/2025 13:30 | 4 | 19 | 2.75 | 6.075 | 1.618 | 7.14 | 53 | 2 | 70.1 | 0.164 | 0.032 | 38.19 | 8975 | 8.37 | 59 |  | 168.89 | 4 | 6.86 | -3.72 | 0.22 | 101
8/26/2025 13:45 | 3 | 19 | 2.75 | 6.122 | 1.611 | 7.14 | 53 | 2 | 70.1 | 0.164 | 0.032 | 38.19 | 8975 | 8.36 | 59 |  | 170.55 | 4.01 | 6.84 | -3.72 | 0.22 | 101
8/26/2025 14:00 | 4 | 19 | 2.75 | 6.098 | 1.507 | 7.13 | 53 | 2 | 70.3 | 0.164 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 167.6 | 3.96 | 6.83 | -3.72 | 0.21 | 101
8/26/2025 14:15 | 5 | 19 | 2.75 | 5.738 | 1.501 | 7.13 | 53 | 2 | 70.3 | 0.164 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 161.04 | 4.04 | 6.83 | -3.72 | 0.23 | 101
8/26/2025 14:30 | 6 | 19 | 2.75 | 6.285 | 1.584 | 7.12 | 53 | 2 | 70.3 | 0.164 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 174.88 | 4.01 | 6.85 | -3.72 | 0.2 | 101
8/26/2025 14:45 | 4 | 19 | 2.75 | 6.193 | 1.576 | 7.12 | 53 | 2 | 70.3 | 0.164 | 0.032 | 38.19 | 8975 | 8.36 | 58 |  | 173.44 | 4.03 | 6.85 | -3.72 | 0.2 | 101
8/26/2025 15:00 | 5 | 19 | 2.75 | 6.244 | 1.708 | 7.12 | 53 | 2 | 70.3 | 0.164 | 0.032 | 38.19 | 8975 | 8.36 | 58 |  | 174.5 | 4.02 | 6.84 | -3.72 | 0.21 | 101
8/26/2025 15:15 | 4 | 19 | 2.75 | 6.187 | 1.854 | 7.11 | 53 | 2 | 70.3 | 0.164 | 0.032 | 38.19 | 8975 | 8.36 | 58 |  | 171.18 | 3.98 | 6.84 | -3.72 | 0.2 | 101
8/26/2025 15:30 | 5 | 19 | 2.75 | 5.865 | 2.026 | 7.1 | 53 | 2 | 70.3 | 0.164 | 0.032 | 38.19 | 8975 | 8.36 | 58 |  | 164.92 | 4.05 | 6.83 | -3.72 | 0.19 | 101
8/26/2025 15:45 | 4 | 19 | 2.75 | 5.914 | 2.174 | 7.1 | 53 | 2 | 70.3 | 0.164 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 164.21 | 4 | 6.83 | -3.72 | 0.19 | 101
8/26/2025 16:00 | 2 | 19 | 2.75 | 6.208 | 2.076 | 7.11 | 53 | 2 | 70.3 | 0.151 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 172.46 | 4 | 6.84 | -3.72 | 0.2 | 101
8/26/2025 16:15 | 5 | 19 | 2.75 | 6.217 | 1.944 | 7.13 | 53 | 2 | 70.3 | 0.151 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 171.87 | 3.98 | 6.86 | -3.72 | 0.23 | 101
8/26/2025 16:30 | 6 | 19 | 2.75 | 6.128 | 1.765 | 7.13 | 53 | 2 | 70.3 | 0.151 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 171.44 | 4.03 | 6.86 | -3.72 | 0.21 | 101
8/26/2025 16:45 | 7 | 19 | 2.75 | 5.67 | 1.676 | 7.14 | 53 | 2 | 70.3 | 0.151 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 158.8 | 4.03 | 6.87 | -3.72 | 0.2 | 101
8/26/2025 17:00 | 7 | 19 | 2.75 | 5.68 | 1.882 | 7.12 | 53 | 2 | 70.3 | 0.151 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 159.56 | 4.05 | 6.85 | -3.72 | 0.21 | 101
8/26/2025 17:15 | 5 | 19 | 2.75 | 6.091 | 1.738 | 7.13 | 53 | 2 | 70.3 | 0.151 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 168.95 | 3.99 | 6.84 | -3.72 | 0.23 | 101
8/26/2025 17:30 | 5 | 19 | 2.75 | 6.124 | 1.959 | 7.12 | 53 | 2 | 70.3 | 0.151 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 168.94 | 3.97 | 6.84 | -3.72 | 0.22 | 101
8/26/2025 17:45 | 4 | 19 | 2.75 | 6.009 | 1.951 | 7.12 | 53 | 2 | 70.3 | 0.151 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 167.88 | 4.02 | 6.83 | -3.72 | 0.22 | 101
8/26/2025 18:00 | 5 | 19 | 2.75 | 6.005 | 2.52 | 7.1 | 53 | 2 | 70.3 | 0.151 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 167.95 | 4.03 | 6.83 | -3.72 | 0.21 | 101
8/26/2025 18:15 | 4 | 19 | 2.75 | 5.611 | 2.801 | 7.09 | 53 | 2 | 70.3 | 0.151 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 157.02 | 4.03 | 6.8 | -3.72 | 0.2 | 101
8/26/2025 18:30 | 3 | 19 | 2.75 | 5.771 | 2.608 | 7.1 | 53 | 2 | 70.3 | 0.151 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 160.79 | 4.01 | 6.81 | -3.72 | 0.21 | 101
8/26/2025 18:45 | 2 | 19 | 2.75 | 6.035 | 2.217 | 7.11 | 53 | 2 | 70.3 | 0.151 | 0.032 | 38.19 | 8975 | 8.37 | 58 |  | 167.68 | 4 | 6.83 | -3.72 | 0.22 | 101
8/26/2025 19:00 | 6 | 19 | 2.75 | 6.015 | 2.202 | 7.11 | 53 | 2 | 70.3 | 0.151 | 0.031 | 38.19 | 8975 | 8.38 | 58 |  | 167.93 | 4.02 | 6.83 | -3.72 | 0.22 | 101
8/26/2025 19:15 | 6 | 19 | 2.75 | 6.015 | 2.037 | 7.11 | 53 | 2 | 70.3 | 0.151 | 0.031 | 38.19 | 8975 | 8.39 | 58 |  | 166.89 | 4 | 6.84 | -3.72 | 0.21 | 101
8/26/2025 19:30 | 5 | 19 | 2.75 | 5.596 | 2.015 | 7.12 | 53 | 2 | 70.3 | 0.151 | 0.031 | 38.19 | 8975 | 8.39 | 58 |  | 155.72 | 4.01 | 6.84 | -3.72 | 0.21 | 101
8/26/2025 19:45 | 6 | 19 | 2.75 | 5.64 | 1.916 | 7.13 | 53 | 2 | 70.3 | 0.151 | 0.031 | 38.19 | 8975 | 8.4 | 58 |  | 156.2 | 3.99 | 6.85 | -3.72 | 0.21 | 101
8/26/2025 20:00 | 4 | 19 | 2.75 | 6.16 | 1.884 | 7.15 | 53 | 2 | 70.3 | 0.182 | 0.031 | 38.19 | 8975 | 8.4 | 58 |  | 170.62 | 3.99 | 6.87 | -3.72 | 0.21 | 101
8/26/2025 20:15 | 4 | 19 | 2.75 | 6.079 | 1.88 | 7.14 | 53 | 2 | 70.3 | 0.182 | 0.031 | 38.19 | 8975 | 8.4 | 58 |  | 167.54 | 3.97 | 6.86 | -3.72 | 0.25 | 101
8/26/2025 20:30 | 4 | 19 | 2.75 | 5.816 | 1.899 | 7.14 | 53 | 2 | 70.3 | 0.182 | 0.031 | 38.19 | 8975 | 8.4 | 58 |  | 163.23 | 4.04 | 6.85 | -3.72 | 0.2 | 101
8/26/2025 20:45 | 3 | 19 | 2.75 | 5.391 | 1.832 | 7.14 | 53 | 2 | 70.3 | 0.182 | 0.031 | 38.19 | 8975 | 8.4 | 58 |  | 147.97 | 3.95 | 6.87 | -3.72 | 0.21 | 101
8/26/2025 21:00 | -1 | 19 | 2.75 | 6.044 | 1.746 | 7.14 | 53 | 2 | 70.3 | 0.182 | 0.031 | 38.19 | 8975 | 8.4 | 58 |  | 168.25 | 4.01 | 6.86 | -3.72 | 0.2 | 101
8/26/2025 21:15 | 4 | 19 | 2.75 | 6.045 | 1.718 | 7.14 | 53 | 2 | 70.3 | 0.182 | 0.031 | 38.19 | 8975 | 8.4 | 58 |  | 168.04 | 4 | 6.85 | -3.72 | 0.21 | 101
8/26/2025 21:30 | 3 | 19 | 2.75 | 6.048 | 1.858 | 7.14 | 53 | 2 | 70.3 | 0.182 | 0.03 | 38.19 | 8975 | 8.4 | 58 |  | 168.12 | 4 | 6.85 | -3.72 | 0.21 | 101
8/26/2025 21:45 | 3 | 19 | 2.75 | 6.014 | 1.789 | 7.14 | 53 | 2 | 70.3 | 0.182 | 0.031 | 38.19 | 8975 | 8.4 | 58 |  | 168.59 | 4.04 | 6.85 | -3.72 | 0.2 | 101
8/26/2025 22:00 | 5 | 19 | 2.75 | 5.508 | 1.858 | 7.13 | 53 | 2 | 70.3 | 0.182 | 0.031 | 38.19 | 8975 | 8.4 | 58 |  | 154.19 | 4.03 | 6.84 | -3.72 | 0.18 | 101
8/26/2025 22:15 | 2 | 19 | 2.75 | 5.551 | 1.899 | 7.13 | 53 | 2 | 70.3 | 0.182 | 0.031 | 38.19 | 8975 | 8.39 | 58 |  | 153.96 | 3.99 | 6.84 | -3.72 | 0.19 | 101
8/26/2025 22:30 | 3 | 19 | 2.75 | 5.863 | 1.949 | 7.12 | 53 | 2 | 70.3 | 0.182 | 0.03 | 38.19 | 8975 | 8.39 | 58 |  | 162.41 | 3.99 | 6.83 | -3.72 | 0.2 | 101
8/26/2025 22:45 | 3 | 19 | 2.75 | 5.821 | 1.931 | 7.11 | 53 | 2 | 70.3 | 0.182 | 0.03 | 38.19 | 8975 | 8.39 | 58 |  | 162.2 | 4.01 | 6.83 | -3.72 | 0.21 | 101
8/26/2025 23:00 | 2 | 19 | 2.75 | 5.829 | 2.073 | 7.1 | 53 | 2 | 70.3 | 0.182 | 0.03 | 38.19 | 8975 | 8.39 | 58 |  | 162.29 | 4.01 | 6.83 | -3.72 | 0.2 | 101
8/26/2025 23:15 | 3 | 19 | 2.75 | 5.828 | 2.172 | 7.09 | 53 | 2 | 70.3 | 0.182 | 0.03 | 38.19 | 8975 | 8.39 | 58 |  | 162.23 | 4.01 | 6.81 | -3.72 | 0.2 | 101
8/26/2025 23:30 | 3 | 19 | 2.75 | 5.816 | 2.266 | 7.08 | 53 | 2 | 70.3 | 0.182 | 0.03 | 38.19 | 8975 | 8.39 | 58 |  | 162.06 | 4.01 | 6.81 | -3.72 | 0.18 | 101
8/26/2025 23:45 | 0 | 19 | 2.75 | 5.914 | 2.246 | 7.08 | 53 | 2 | 70.3 | 0.182 | 0.03 | 38.19 | 8975 | 8.39 | 58 |  | 161.92 | 3.94 | 6.81 | -3.72 | 0.2 | 101
8/27/2025 00:00 | 3 | 19 | 2.75 | 5.825 | 2.175 | 7.09 | 53 | 2 | 70.3 | 0.211 | 0.03 | 38.19 | 8975 | 8.39 | 58 | 1.5 | 161.57 | 3.99 | 6.82 | -3.72 | 0.2 | 101
8/27/2025 00:15 | 3 | 19 | 2.75 | 5.281 | 2.091 | 7.1 | 53 | 2 | 70.3 | 0.211 | 0.03 | 38.19 | 8975 | 8.39 | 58 | 1.5 | 147.26 | 4.02 | 6.83 | -3.72 | 0.19 | 101
8/27/2025 00:30 | 2 | 19 | 2.75 | 5.836 | 1.876 | 7.11 | 53 | 2 | 70.3 | 0.211 | 0.03 | 38.19 | 8975 | 8.4 | 58 | 1.5 | 161.53 | 3.99 | 6.84 | -3.72 | 0.2 | 101
8/27/2025 00:45 | 4 | 19 | 2.75 | 6.119 | 1.814 | 7.11 | 53 | 2 | 70.3 | 0.211 | 0.03 | 38.19 | 8975 | 8.39 | 58 | 1.5 | 170.35 | 4.01 | 6.84 | -3.72 | 0.2 | 101
8/27/2025 01:00 | 1 | 19 | 2.75 | 5.972 | 1.827 | 7.11 | 53 | 2 | 70.3 | 0.211 | 0.03 | 38.57 | 8880 | 8.4 | 58 | 1.5 | 167.75 | 4.04 | 6.83 | -3.72 | 0.2 | 101
8/27/2025 01:15 | 0 | 19 | 2.75 | 6.322 | 2.218 | 7.11 | 53 | 2 | 70.3 | 0.211 | 0.03 | 38.57 | 8880 | 8.4 | 58 | 1.5 | 175.66 | 4 | 6.83 | -3.72 | 0.2 | 101
8/27/2025 01:30 | 3 | 19 | 2.75 | 6.328 | 1.809 | 7.1 | 53 | 2 | 70.3 | 0.211 | 0.032 | 38.57 | 8880 | 8.4 | 58 | 1.5 | 175.34 | 3.99 | 6.83 | -3.72 | 0.2 | 101
8/27/2025 01:45 | 3 | 19 | 2.75 | 5.739 | 1.759 | 7.1 | 53 | 2 | 70.3 | 0.211 | 0.032 | 38.57 | 8880 | 8.39 | 58 | 1.5 | 159.35 | 4 | 6.83 | -3.72 | 0.2 | 101
8/27/2025 02:00 | 3 | 19 | 2.75 | 5.771 | 1.755 | 7.1 | 53 | 2 | 70.1 | 0.211 | 0.032 | 38.57 | 8880 | 8.4 | 56 | 1.5 | 159.93 | 3.99 | 6.83 | -3.72 | 0.2 | 101
8/27/2025 02:15 | 2 | 19 | 2.75 | 5.973 | 1.724 | 7.1 | 53 | 2 | 70.1 | 0.211 | 0.032 | 38.57 | 8880 | 8.39 | 56 | 1.5 | 168.39 | 4.06 | 6.83 | -3.72 | 0.19 | 101
8/27/2025 02:30 | 4 | 19 | 2.75 | 6.413 | 1.577 | 7.1 | 53 | 2 | 70.1 | 0.211 | 0.032 | 38.57 | 8880 | 8.37 | 56 | 1.5 | 176.25 | 3.96 | 6.82 | -3.72 | 0.21 | 101
8/27/2025 02:45 | 1 | 19 | 2.75 | 6.347 | 1.613 | 7.1 | 53 | 2 | 70.1 | 0.211 | 0.032 | 38.57 | 8880 | 8.36 | 56 | 1.5 | 176.21 | 4 | 6.81 | -3.72 | 0.21 | 101
8/27/2025 03:00 | 1 | 19 | 2.75 | 5.832 | 1.66 | 7.1 | 53 | 2 | 70.1 | 0.211 | 0.032 | 38.57 | 8880 | 8.38 | 56 | 1.5 | 161.29 | 3.98 | 6.79 | -3.72 | 0.19 | 101
8/27/2025 03:15 | 4 | 19 | 2.75 | 5.848 | 1.676 | 7.1 | 53 | 2 | 70.1 | 0.211 | 0.032 | 38.57 | 8880 | 8.4 | 56 | 1.5 | 161.96 | 3.99 | 6.79 | -3.72 | 0.2 | 101
8/27/2025 03:30 | 3 | 19 | 2.75 | 6.167 | 1.755 | 7.09 | 53 | 2 | 70.1 | 0.211 | 0.031 | 38.57 | 8880 | 8.43 | 56 | 1.5 | 170.82 | 3.99 | 6.79 | -3.72 | 0.2 | 101
8/27/2025 03:45 | 3 | 19 | 2.75 | 6.476 | 1.858 | 7.09 | 53 | 2 | 70.1 | 0.211 | 0.031 | 38.57 | 8880 | 8.44 | 56 | 1.5 | 176.49 | 3.92 | 6.79 | -3.72 | 0.19 | 101
8/27/2025 04:00 | 0 | 19 | 2.75 | 6.121 | 2.014 | 7.08 | 53 | 2 | 70.1 | 0.229 | 0.031 | 38.57 | 8880 | 8.44 | 56 | 1.5 | 170.23 | 4 | 6.79 | -3.72 | 0.18 | 101
8/27/2025 04:15 | 0 | 19 | 2.75 | 6.07 | 1.999 | 7.08 | 53 | 2 | 70.1 | 0.229 | 0.031 | 38.57 | 8880 | 8.43 | 56 | 1.5 | 168.24 | 3.99 | 6.8 | -3.72 | 0.19 | 101
8/27/2025 04:30 | 4 | 19 | 2.75 | 6.084 | 2.118 | 7.07 | 53 | 2 | 70.1 | 0.229 | 0.031 | 38.57 | 8880 | 8.43 | 56 | 1.5 | 168.17 | 3.98 | 6.81 | -3.72 | 0.18 | 101
8/27/2025 04:45 | 1 | 19 | 2.75 | 6.249 | 2.077 | 7.08 | 53 | 2 | 70.1 | 0.229 | 0.031 | 38.57 | 8880 | 8.42 | 56 | 1.5 | 173.44 | 4 | 6.81 | -3.72 | 0.19 | 101
8/27/2025 05:00 | 1 | 19 | 2.75 | 6.214 | 2.103 | 7.08 | 53 | 2 | 70.1 | 0.229 | 0.031 | 38.57 | 8880 | 8.41 | 56 | 1.5 | 172.61 | 4 | 6.82 | -3.72 | 0.15 | 101
8/27/2025 05:15 | 3 | 19 | 2.75 | 6.311 | 2.129 | 7.08 | 53 | 2 | 70.1 | 0.229 | 0.031 | 38.57 | 8880 | 8.41 | 56 | 1.5 | 174.39 | 3.98 | 6.82 | -3.72 | 0.15 | 101
8/27/2025 05:30 | -3 | 19 | 2.75 | 6.319 | 2.169 | 7.07 | 53 | 2 | 70.1 | 0.229 | 0.031 | 38.57 | 8880 | 8.41 | 56 | 1.5 | 175.13 | 3.99 | 6.82 | -3.72 | 0.17 | 101
8/27/2025 05:45 | 2 | 19 | 2.75 | 6.301 | 2.236 | 7.07 | 53 | 2 | 70.1 | 0.229 | 0.031 | 38.57 | 8880 | 8.4 | 56 | 1.5 | 174.64 | 3.99 | 6.81 | -3.72 | 0.17 | 101
8/27/2025 06:00 | 2 | 19 | 2.75 | 5.955 | 2.274 | 7.07 | 53 | 2 | 70.1 | 0.229 | 0.031 | 38.57 | 8880 | 8.39 | 56 | 1.5 | 165.12 |  | 6.81 | -3.72 | 0.16 | 101
8/27/2025 06:15 | 3 | 19 | 2.75 | 5.966 | 2.339 | 7.06 | 53 | 2 | 70.1 | 0.229 | 0.031 | 38.57 | 8880 | 8.39 | 56 | 1.5 | 165.78 |  | 6.81 | -3.72 | 0.16 | 101
8/27/2025 06:30 | 4 | 19 | 2.75 | 6.556 | 2.265 | 7.07 | 53 | 2 | 70.1 | 0.229 | 0.03 | 38.57 | 8880 | 8.38 | 56 | 1.5 | 176.51 |  | 6.81 | -3.72 | 0.16 | 101
8/27/2025 06:45 | -5 | 19 | 2.75 | 6.515 | 2.217 | 7.07 | 53 | 2 | 70.1 | 0.229 | 0.03 | 38.57 | 8880 | 8.39 | 56 | 1.5 | 176.22 |  | 6.81 | -3.72 | 0.18 | 101
8/27/2025 07:00 | 0 | 19 | 2.75 | 6.057 | 2.188 | 7.08 | 53 | 2 | 70.1 | 0.229 | 0.03 | 38.57 | 8880 | 8.39 | 56 | 1.5 | 168.15 |  | 6.82 | -3.72 | 0.18 | 101
8/27/2025 07:15 | 2 | 19 | 2.75 | 6.04 | 2.131 | 7.08 | 53 | 2 | 70.1 | 0.229 | 0.03 | 38.57 | 8880 | 8.38 | 56 | 1.5 | 168.25 |  | 6.82 | -3.72 | 0.16 | 101
8/27/2025 07:30 | 4 | 19 | 2.75 | 6.22 | 2.074 | 7.08 | 53 | 2 | 70.1 | 0.229 | 0.03 | 38.57 | 8880 | 8.38 | 56 | 1.5 | 174.36 |  | 6.82 | -3.72 | 0.16 | 101
8/27/2025 07:45 | -2 | 19 | 2.75 | 6.528 | 1.964 | 7.09 | 53 | 2 | 70.1 | 0.229 | 0.03 | 38.57 | 8880 | 8.38 | 56 | 1.5 | 44.13 |  | 6.83 | -3.72 | 0.16 | 101
8/27/2025 08:00 | 1 | 19 | 2.75 | 6.503 | 2.171 | 7.08 | 53 | 2 | 70.1 | 0.246 | 0.03 | 38.57 | 8880 | 8.38 | 56 | 1.5 | 179.64 |  | 6.83 | -3.72 | 0.18 | 101
8/27/2025 08:15 | -2 | 19 | 2.75 | 5.789 | 1.964 | 7.08 | 53 | 2 | 70.1 | 0.246 | 0.03 | 38.57 | 8880 | 8.37 | 56 | 1.5 | 161.9 |  | 6.83 | -3.72 | 0.15 | 101
8/27/2025 08:30 | -7 | 19 | 2.75 | 5.838 | 1.883 | 7.08 | 53 | 2 | 70.1 | 0.246 | 0.03 | 38.57 | 8880 | 8.37 | 56 | 1.5 | 160.87 |  | 6.82 | -3.72 | 0.18 | 101
8/27/2025 08:45 | -4 | 19 | 2.75 | 6.372 | 1.825 | 7.08 | 53 | 2 | 70.1 | 0.246 | 0.03 | 38.57 | 8880 | 8.37 | 56 | 1.5 | 177.12 |  | 6.82 | -3.72 | 0.21 | 101
8/27/2025 09:00 | -4 | 19 | 2.75 | 6.372 | 1.968 | 7.07 | 53 | 2 | 70.1 | 0.246 | 0.03 | 38.57 | 8880 | 8.36 | 56 | 1.5 | 176.77 |  | 6.82 | -3.72 | 0.16 | 101
8/27/2025 09:15 | -6 | 21 | 2.75 | 5.88 | 2.014 | 7.06 | 53 | 2 | 70.1 | 0.246 | 0.03 | 38.57 | 8880 | 8.36 | 56 | 1.5 | 163.82 |  | 6.79 | -3.72 | 0.17 | 101
8/27/2025 09:30 | 3 | 21 | 2.75 | 5.886 | 2.053 | 7.05 | 53 | 2 | 70.1 | 0.246 | 0.03 | 38.57 | 8880 | 8.35 | 56 | 1.5 | 163.28 |  | 6.78 | -3.72 | 0.15 | 101
8/27/2025 09:45 | 1 | 21 | 2.75 | 5.707 | 2.089 | 7.05 | 53 | 2 | 70.1 | 0.246 | 0.03 | 38.57 | 8880 | 8.35 | 56 | 1.5 | 157.86 |  | 6.79 | -3.72 | 0.15 | 101
8/27/2025 10:00 | 3 | 21 | 2.75 | 6.135 | 2.105 | 7.05 | 54 | 2 | 69.9 | 0.246 | 0.03 | 38.57 | 8880 | 8.35 | 56 | 1.5 | 170.16 |  | 6.79 | -3.72 | 0.17 | 101
8/27/2025 10:15 | 4 | 21 | 2.75 | 6.267 | 2.096 | 7.05 | 54 | 2 | 69.9 | 0.246 | 0.03 | 38.57 | 8880 | 8.35 | 56 | 1.5 | 173.58 |  | 6.8 | -3.72 | 0.19 | 101
8/27/2025 10:30 | 2 | 21 | 2.75 | 5.822 | 2.038 | 7.06 | 54 | 2 | 69.9 | 0.246 | 0.029 | 38.57 | 8880 | 8.35 | 56 | 1.5 | 160.48 |  | 6.79 | -3.72 | 0.17 | 101
8/27/2025 10:45 | 4 | 21 | 2.75 | 5.261 | 2.043 | 7.06 | 54 | 2 | 69.9 | 0.246 | 0.029 | 38.57 | 8880 | 8.34 | 56 | 1.5 | 163.28 |  | 6.79 | -3.72 | 0.21 | 101
8/27/2025 11:00 | 2 | 21 | 2.75 | 5.248 | 2.059 | 7.07 | 54 | 2 | 69.9 | 0.246 | 0.029 | 38.57 | 8880 | 8.34 | 56 | 1.5 | 163.88 |  | 6.79 | -3.72 | 0.18 | 101
8/27/2025 11:15 | 2 | 21 | 2.75 | 5.279 | 2.047 | 7.07 | 54 | 2 | 69.9 | 0.246 | 0.029 | 38.57 | 8880 | 8.34 | 56 | 1.5 | 164.14 |  | 6.79 | -3.72 | 0.18 | 101
8/27/2025 11:30 | 0 | 21 | 2.75 | 5.573 | 2.139 | 7.07 | 54 | 2 | 69.9 | 0.246 | 0.029 | 38.57 | 8880 | 8.34 | 56 | 1.5 | 173.3 |  | 6.78 | -3.72 | 0.18 | 101
8/27/2025 11:45 | 2 | 21 | 2.75 | 5.827 | 2.169 | 7.07 | 54 | 2 | 69.9 | 0.246 | 0.029 | 38.57 | 8880 | 8.34 | 56 | 1.5 | 180.49 |  | 6.79 | -3.72 | 0.2 | 101
8/27/2025 12:00 | -1 | 21 | 2.75 | 5.371 | 2.335 | 7.01 | 54 | 2 | 69.9 | 0.168 | 0.029 | 38.57 | 8880 | 8.35 | 56 | 1.5 | 94.18 |  | 6.72 | -3.72 | 0.21 | 101
8/27/2025 12:15 | 1 | 21 | 2.75 | 5.056 | 2.659 | 7.04 | 54 | 2 | 69.9 | 0.168 | 0.029 | 38.57 | 8880 | 8.35 | 56 | 1.5 | 87.22 |  | 6.73 | -3.72 | 0.22 | 101
8/27/2025 12:30 | 0 | 21 | 2.75 | 4.988 | 2.454 | 7.06 | 54 | 2 | 69.9 | 0.168 | 0.029 | 38.57 | 8880 | 8.35 | 56 | 1.5 | 87.39 |  | 6.81 | -3.72 | 0.23 | 101
8/27/2025 12:45 | 0 | 21 | 2.75 | 5.625 | 2.447 | 7.07 | 54 | 2 | 69.9 | 0.168 | 0.029 | 38.57 | 8880 | 8.36 | 56 | 1.5 | 97.78 |  | 6.79 | -3.72 | 0.23 | 101
8/27/2025 13:00 | 2 | 21 | 2.75 | 5.636 | 2.448 | 7.07 | 54 | 2 | 69.9 | 0.168 | 0.029 | 38.57 | 8880 | 8.35 | 56 | 1.5 | 97.77 |  | 6.79 | -3.72 | 0.21 | 101
8/27/2025 13:15 | 1 | 21 | 2.75 | 5.594 | 2.377 | 7.07 | 54 | 2 | 69.9 | 0.168 | 0.029 | 38.57 | 8880 | 8.36 | 56 | 1.5 | 97.51 |  | 6.79 | -3.72 | 0.22 | 101
8/27/2025 13:30 | 2 | 21 | 2.75 | 5.151 | 1.928 | 7.1 | 54 | 2 | 69.9 | 0.168 | 0.029 | 38.57 | 8880 | 8.36 | 56 | 1.5 | 89.41 |  | 6.82 | -3.72 | 0.22 | 101
8/27/2025 13:45 | 1 | 21 | 2.75 | 5.164 | 1.727 | 7.14 | 54 | 2 | 69.9 | 0.168 | 0.029 | 38.57 | 8880 | 8.36 | 56 | 1.5 | 89.04 |  | 6.85 | -3.72 | 0.21 | 101
8/27/2025 14:00 | 0 | 21 | 2.75 | 5.614 | 1.743 | 7.13 | 54 | 2 | 70.3 | 0.168 | 0.029 | 38.57 | 8880 | 8.37 | 56 | 1.5 | 97.89 |  | 6.84 | -3.72 | 0.21 | 101
8/27/2025 14:15 | 0 | 21 | 2.75 | 5.636 | 1.453 | 7.14 | 54 | 2 | 70.3 | 0.168 | 0.028 | 38.57 | 8880 | 8.37 | 56 | 1.5 | 98.41 |  | 6.83 | -3.72 | 0.21 | 101
8/27/2025 14:30 | 1 | 21 | 2.75 | 5.632 | 1.8 | 7.11 | 54 | 2 | 70.3 | 0.168 | 0.029 | 38.57 | 8880 | 8.37 | 56 | 1.5 | 97.61 |  | 6.8 | -3.72 | 0.21 | 101
8/27/2025 14:45 | 4 | 21 | 2.75 | 5.297 | 1.854 | 7.08 | 54 | 2 | 70.3 | 0.168 | 0.028 | 38.57 | 8880 | 8.37 | 56 | 1.5 | 92.33 |  | 6.78 | -3.72 | 0.21 | 101
8/27/2025 15:00 | 5 | 21 | 2.75 | 5.055 | 2.077 | 7.06 | 54 | 2 | 70.3 | 0.168 | 0.028 | 38.57 | 8880 | 8.37 | 56 | 1.5 | 87.37 |  | 6.79 | -3.72 | 0.22 | 101
8/27/2025 15:15 | 5 | 21 | 2.75 | 5.606 | 2.06 | 7.06 | 54 | 2 | 70.3 | 0.168 | 0.028 | 38.57 | 8880 | 8.37 | 56 | 1.5 | 97.5 |  | 6.79 | -3.72 | 0.19 | 101
8/27/2025 15:30 | 3 | 21 | 2.75 | 5.627 | 2.118 | 7.06 | 54 | 2 | 70.3 | 0.168 | 0.028 | 38.57 | 8880 | 8.38 | 56 | 1.5 | 97.85 |  | 6.77 | -3.72 | 0.2 | 101
8/27/2025 15:45 | 3 | 21 | 2.75 | 5.649 | 2.258 | 7.04 | 54 | 2 | 70.3 | 0.168 | 0.028 | 38.57 | 8880 | 8.38 | 56 | 1.5 | 97.71 |  | 6.75 | -3.72 | 0.2 | 101
8/27/2025 16:00 | 5 | 21 | 2.75 | 3.732 | 2.223 | 7.05 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.57 | 8880 | 8.38 | 56 | 1.5 | 64.89 |  | 6.75 | -3.72 | 0.2 | 101
8/27/2025 16:15 | 3 | 21 | 2.75 | 4.428 | 2.01 | 7.08 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.38 | 56 | 1.5 | 77.15 |  | 6.79 | -3.72 | 0.2 | 101
8/27/2025 16:30 | 4 | 21 | 2.75 | 4.441 | 1.715 | 7.11 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.38 | 56 | 1.5 | 77.43 |  | 6.82 | -3.72 | 0.2 | 101
8/27/2025 16:45 | 1 | 21 | 2.75 | 4.062 | 1.338 | 7.16 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.38 | 56 | 1.5 | 70.16 |  | 6.85 | -3.72 | 0.2 | 101
8/27/2025 17:00 | 4 | 21 | 2.75 | 4.052 | 1.193 | 7.17 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.38 | 56 | 1.5 | 70.42 |  | 6.87 | -3.72 | 0.18 | 101
8/27/2025 17:15 | 3 | 21 | 2.75 | 4.083 | 1.649 | 7.12 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.38 | 56 | 1.5 | 70.5 |  | 6.83 | -3.72 | 0.18 | 101
8/27/2025 17:30 | 3 | 21 | 2.75 | 4.464 | 2.268 | 7.06 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.38 | 56 | 1.5 | 77.3 |  | 6.76 | -3.72 | 0.18 | 101
8/27/2025 17:45 | 2 | 21 | 2.75 | 4.308 | 2.364 | 7.04 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.37 | 56 | 1.5 | 75.57 |  | 6.75 | -3.72 | 0.2 | 101
8/27/2025 18:00 | 3 | 21 | 2.75 | 3.757 | 2.313 | 7.04 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.36 | 56 | 1.5 | 65.71 |  | 6.73 | -3.72 | 0.2 | 101
8/27/2025 18:15 | 3 | 21 | 2.75 | 3.805 | 2.366 | 7.07 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.34 | 56 | 1.5 | 65.46 |  | 6.74 | -3.72 | 0.2 | 101
8/27/2025 18:30 | 5 | 21 | 2.75 | 3.846 | 2.475 | 7.08 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.32 | 56 | 1.5 | 66.81 |  | 6.77 | -3.72 | 0.19 | 101
8/27/2025 18:45 | 0 | 21 | 2.75 | 4.4 | 2.574 | 7.09 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.3 | 56 | 1.5 | 76.05 |  | 6.77 | -3.72 | 0.21 | 101
8/27/2025 19:00 | 2 | 21 | 2.75 | 4.373 | 2.514 | 7.1 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.29 | 56 | 1.5 | 76.05 |  | 6.8 | -3.72 | 0.2 | 101
8/27/2025 19:15 | 5 | 21 | 2.75 | 3.775 | 2.47 | 7.1 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.29 | 56 | 1.5 | 65.52 |  | 6.8 | -3.72 | 0.21 | 101
8/27/2025 19:30 | 6 | 21 | 2.75 | 3.785 | 2.504 | 7.1 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.29 | 56 | 1.5 | 65.75 |  | 6.79 | -3.72 | 0.19 | 101
8/27/2025 19:45 | 5 | 21 | 2.75 | 4.108 | 2.458 | 7.11 | 54 | 2 | 70.3 | 0.151 | 0.029 | 38.75 | 8887 | 8.3 | 56 | 1.5 | 71.12 |  | 6.79 | -3.72 | 0.2 | 101
8/27/2025 20:00 | 5 | 21 | 2.75 | 4.126 | 2.234 | 7.13 | 54 | 2 | 70.3 | 0.156 | 0.029 | 38.75 | 8887 | 8.32 | 56 | 1.5 | 70.65 |  | 6.81 | -3.72 | 0.2 | 101
8/27/2025 20:15 | 5 | 21 | 2.75 | 4.109 | 2.047 | 7.14 | 54 | 2 | 70.3 | 0.156 | 0.029 | 38.75 | 8887 | 8.33 | 56 | 1.5 | 71.04 |  | 6.83 | -3.72 | 0.19 | 101
8/27/2025 20:30 | 4 | 21 | 2.75 | 4.105 | 1.84 | 7.15 | 54 | 2 | 70.3 | 0.156 | 0.029 | 38.75 | 8887 | 8.34 | 56 | 1.5 | 71.26 |  | 6.83 | -3.72 | 0.19 | 101
8/27/2025 20:45 | 2 | 21 | 2.75 | 4.099 | 1.807 | 7.14 | 54 | 2 | 70.3 | 0.156 | 0.029 | 38.75 | 8887 | 8.34 | 56 | 1.5 | 71.04 |  | 6.83 | -3.72 | 0.2 | 101
8/27/2025 21:00 | 5 | 21 | 2.75 | 3.975 | 1.897 | 7.1 | 54 | 2 | 70.3 | 0.156 | 0.029 | 38.75 | 8887 | 8.35 | 56 | 1.5 | 69.12 |  | 6.79 | -3.72 | 0.2 | 101
8/27/2025 21:15 | 5 | 21 | 2.75 | 3.671 | 1.871 | 7.09 | 54 | 2 | 70.3 | 0.156 | 0.029 | 38.75 | 8887 | 8.35 | 56 | 1.5 | 63.58 |  | 6.78 | -3.72 | 0.19 | 101
8/27/2025 21:30 | 5 | 21 | 2.75 | 4.212 | 1.982 | 7.08 | 54 | 2 | 70.3 | 0.156 | 0.029 | 38.75 | 8887 | 8.36 | 56 | 1.5 | 73.21 |  | 6.77 | -3.72 | 0.2 | 101
8/27/2025 21:45 | 4 | 21 | 2.75 | 4.224 | 2.055 | 7.09 | 54 | 2 | 70.3 | 0.156 | 0.029 | 38.75 | 8887 | 8.36 | 56 | 1.5 | 72.98 |  | 6.78 | -3.72 | 0.2 | 101
8/27/2025 22:00 | 5 | 21 | 2.75 | 4.231 | 2.052 | 7.1 | 56 | 2 | 70.3 | 0.156 | 0.029 | 38.75 | 8887 | 8.36 | 56 | 1.5 | 73.14 |  | 6.78 | -3.72 | 0.2 | 101
8/27/2025 22:15 | 5 | 21 | 2.75 | 4.484 | 1.959 | 7.12 | 56 | 2 | 70.3 | 0.156 | 0.029 | 38.75 | 8887 | 8.36 | 56 | 1.5 | 78.34 |  | 6.81 | -3.72 | 0.22 | 101
8/27/2025 22:30 | 6 | 21 | 2.75 | 4.465 | 1.864 | 7.11 | 56 | 2 | 70.3 | 0.156 | 0.029 | 38.49 | 8906 | 8.35 | 56 | 1.5 | 77.99 |  | 6.81 | -3.72 | 0.21 | 101
8/27/2025 22:45 | 6 | 21 | 2.75 | 4.487 | 1.832 | 7.1 | 56 | 2 | 70.3 | 0.156 | 0.03 | 38.49 | 8906 | 8.35 | 56 | 1.5 | 78.03 |  | 6.8 | -3.72 | 0.21 | 101
8/27/2025 23:00 | 7 | 21 | 2.75 | 5.034 | 1.789 | 7.1 | 56 | 2 | 70.3 | 0.156 | 0.031 | 38.49 | 8906 | 8.35 | 56 | 1.5 | 87.89 |  | 6.79 | -3.72 | 0.21 | 101
8/27/2025 23:15 | 6 | 21 | 2.75 | 5.061 | 1.98 | 7.09 | 56 | 2 | 70.3 | 0.156 | 0.033 | 38.49 | 8906 | 8.34 | 56 | 1.5 | 86.77 |  | 6.82 | -3.72 | 0.19 | 101
8/27/2025 23:30 | 8 | 21 | 2.75 | 4.295 | 1.695 | 7.09 | 56 | 2 | 70.3 | 0.156 | 0.033 | 38.49 | 8906 | 8.34 | 56 | 1.5 | 74.82 |  | 6.81 | -3.72 | 0.19 | 101
8/27/2025 23:45 | 7 | 21 | 2.75 | 4.288 | 1.588 | 7.09 | 56 | 2 | 70.3 | 0.156 | 0.034 | 38.49 | 8906 | 8.33 | 56 | 1.5 | 74.79 |  | 6.79 | -3.72 | 0.18 | 101
8/28/2025 00:00 | 7 | 21 | 2.75 | 4.28 | 1.636 | 7.07 | 56 | 1.96 | 70.3 | 0.185 | 0.034 | 38.49 | 8906 | 8.33 | 56 |  | 74.88 |  | 6.79 | -3.72 | 0.18 | 101
8/28/2025 00:15 | 5 | 21 | 2.75 | 4.618 | 1.719 | 7.06 | 56 | 1.96 | 70.3 | 0.185 | 0.034 | 38.49 | 8906 | 8.31 | 56 |  | 80.27 |  | 6.77 | -3.72 | 0.19 | 101
8/28/2025 00:30 | 3 | 21 | 2.75 | 6.255 | 1.833 | 7.05 | 56 | 1.96 | 70.3 | 0.185 | 0.034 | 38.49 | 8906 | 8.29 | 56 |  | 107.5 |  | 6.78 | -3.72 | 0.2 | 101
8/28/2025 00:45 | 2 | 21 | 2.75 | 6.352 | 1.804 | 7.06 | 56 | 1.96 | 70.3 | 0.185 | 0.034 | 38.49 | 8906 | 8.27 | 56 |  | 111.45 |  | 6.8 | -3.72 | 0.2 | 101
8/28/2025 01:00 | 5 | 21 | 2.75 | 6.341 | 1.763 | 7.07 | 56 | 1.96 | 70.3 | 0.185 | 0.034 | 38.49 | 8906 | 8.28 | 56 |  | 111.5 |  | 6.8 | -3.72 | 0.2 | 101
8/28/2025 01:15 | 4 | 21 | 2.75 | 5.852 | 1.722 | 7.08 | 56 | 1.96 | 70.3 | 0.185 | 0.035 | 38.49 | 8906 | 8.3 | 56 |  | 99.79 |  | 6.79 | -3.72 | 0.2 | 101
8/28/2025 01:30 | 4 | 21 | 2.75 | 5.875 | 1.569 | 7.1 | 56 | 1.96 | 70.3 | 0.185 | 0.035 | 38.49 | 8906 | 8.31 | 56 |  | 103.15 |  | 6.8 | -3.72 | 0.18 | 101
8/28/2025 01:45 | 6 | 21 | 2.75 | 6.342 | 1.561 | 7.11 | 56 | 1.96 | 70.3 | 0.185 | 0.035 | 38.49 | 8906 | 8.31 | 56 |  | 110.82 |  | 6.82 | -3.72 | 0.19 | 101
8/28/2025 02:00 | 4 | 21 | 2.75 | 6.287 | 1.574 | 7.11 | 56 | 1.96 | 70.1 | 0.185 | 0.035 | 38.49 | 8906 | 8.3 | 55 |  | 110.02 |  | 6.82 | -3.72 | 0.18 | 101
8/28/2025 02:15 | 4 | 21 | 2.75 | 5.972 | 1.616 | 7.11 | 56 | 1.96 | 70.1 | 0.185 | 0.035 | 38.49 | 8906 | 8.32 | 55 |  | 104.58 |  | 6.81 | -3.72 | 0.18 | 101
8/28/2025 02:30 | 7 | 21 | 2.75 | 5.91 | 1.81 | 7.09 | 56 | 1.96 | 70.1 | 0.185 | 0.035 | 38.49 | 8906 | 8.34 | 55 |  | 102.56 |  | 6.79 | -3.72 | 0.16 | 101
8/28/2025 02:45 | 7 | 21 | 2.75 | 6.105 | 1.896 | 7.09 | 56 | 1.96 | 70.1 | 0.185 | 0.035 | 38.49 | 8906 | 8.37 | 55 |  | 106.66 |  | 6.78 | -3.72 | 0.16 | 101
8/28/2025 03:00 | 2 | 21 | 2.75 | 6.138 | 1.978 | 7.08 | 56 | 1.96 | 70.1 | 0.185 | 0.034 | 38.49 | 8906 | 8.39 | 55 |  | 106.51 |  | 6.78 | -3.72 | 0.17 | 101
8/28/2025 03:15 | 3 | 21 | 2.75 | 6.174 | 1.956 | 7.07 | 56 | 1.96 | 70.1 | 0.185 | 0.034 | 38.49 | 8906 | 8.4 | 55 |  | 106.25 |  | 6.78 | -3.72 | 0.17 | 101
8/28/2025 03:30 | 4 | 21 | 2.75 | 6.165 | 1.834 | 7.06 | 56 | 1.96 | 70.1 | 0.185 | 0.034 | 38.49 | 8906 | 8.39 | 55 |  | 106.46 |  | 6.76 | -3.72 | 0.18 | 101
8/28/2025 03:45 | 4 | 21 | 2.75 | 6.154 | 1.719 | 7.06 | 56 | 1.96 | 70.1 | 0.185 | 0.034 | 38.49 | 8906 | 8.38 | 55 |  | 106.51 |  | 6.77 | -3.72 | 0.18 | 101
8/28/2025 04:00 | 2 | 21 | 2.75 | 6.111 | 1.648 | 7.06 | 56 | 1.96 | 70.1 | 0.231 | 0.034 | 38.49 | 8906 | 8.35 | 55 |  | 105.93 |  | 6.77 | -3.72 | 0.19 | 101
8/28/2025 04:15 | 4 | 21 | 2.75 | 6.113 | 1.605 | 7.07 | 56 | 1.96 | 70.1 | 0.231 | 0.034 | 39.29 | 8904 | 8.33 | 55 |  | 105.15 |  | 6.77 | -3.72 | 0.17 | 101
8/28/2025 04:30 | 0 | 21 | 2.75 | 5.524 | 1.633 | 7.06 | 56 | 1.96 | 70.1 | 0.231 | 0.035 | 39.29 | 8904 | 8.31 | 55 |  | 95.57 |  | 6.77 | -3.72 | 0.17 | 101
8/28/2025 04:45 | 3 | 21 | 2.75 | 5.804 | 1.606 | 7.06 | 56 | 1.96 | 70.1 | 0.231 | 0.035 | 39.29 | 8904 | 8.29 | 55 |  | 100.36 |  | 6.76 | -3.72 | 0.17 | 101
8/28/2025 05:00 | 6 | 21 | 2.75 | 6.103 | 1.621 | 7.07 | 56 | 1.96 | 70.1 | 0.231 | 0.036 | 39.29 | 8904 | 8.28 | 55 |  | 105.7 |  | 6.76 | -3.72 | 0.2 | 101
8/28/2025 05:15 | 3 | 21 | 2.75 | 6.042 | 1.608 | 7.07 | 56 | 1.96 | 70.1 | 0.231 | 0.036 | 39.29 | 8904 | 8.28 | 55 |  | 105.06 |  | 6.77 | -3.72 | 0.17 | 101
8/28/2025 05:30 | 3 | 21 | 2.75 | 6.074 | 1.698 | 7.06 | 56 | 1.96 | 70.1 | 0.231 | 0.036 | 39.29 | 8904 | 8.25 | 55 |  | 105.4 |  | 6.76 | -3.72 | 0.18 | 101
8/28/2025 05:45 | 4 | 21 | 2.75 | 6.062 | 1.78 | 7.06 | 56 | 1.96 | 70.1 | 0.231 | 0.036 | 39.29 | 8904 | 8.23 | 55 |  | 104.93 |  | 6.76 | -3.72 | 0.19 | 101
8/28/2025 06:00 | 3 | 21 | 2.75 | 6.042 | 2.2 | 7.07 | 56 | 1.96 | 70.1 | 0.231 | 0.036 | 39.29 | 8904 | 8.21 | 55 |  | 105.23 |  | 6.77 | -3.72 | 0.19 | 101
8/28/2025 06:15 | 3 | 21 | 2.75 | 5.95 | 1.931 | 7.08 | 56 | 1.96 | 70.1 | 0.231 | 0.036 | 39.29 | 8904 | 8.21 | 55 |  | 104.32 |  | 6.77 | -3.72 | 0.18 | 101
8/28/2025 06:30 | 1 | 21 | 2.75 | 5.945 | 1.853 | 7.08 | 56 | 1.96 | 70.1 | 0.231 | 0.036 | 39.29 | 8904 | 8.23 | 55 |  | 102.54 |  | 6.78 | -3.72 | 0.19 | 101
8/28/2025 06:45 | 1 | 21 | 2.75 | 5.898 | 1.813 | 7.09 | 56 | 1.96 | 70.1 | 0.231 | 0.036 | 39.29 | 8904 | 8.25 | 55 |  | 101.98 |  | 6.79 | -3.72 | 0.17 | 101
8/28/2025 07:00 | 2 | 21 | 2.75 | 5.947 | 1.852 | 7.09 | 56 | 1.96 | 70.1 | 0.231 | 0.035 | 39.29 | 8904 | 8.26 | 55 |  | 102.98 |  | 6.8 | -3.72 | 0.17 | 101
8/28/2025 07:15 | -1 | 21 | 2.75 | 6.139 | 1.82 | 7.09 | 56 | 1.96 | 70.1 | 0.231 | 0.035 | 39.29 | 8904 | 8.26 | 55 |  | 106.4 |  | 6.8 | -3.72 | 0.18 | 101
8/28/2025 07:30 | 0 | 21 | 2.75 | 6.157 | 1.845 | 7.09 | 56 | 1.96 | 70.1 | 0.231 | 0.035 | 39.29 | 8904 | 8.26 | 55 |  | 105.9 |  | 6.8 | -3.72 | 0.19 | 101
8/28/2025 07:45 | 1 | 21 | 2.75 | 6.072 | 1.752 | 7.09 | 56 | 1.96 | 70.1 | 0.231 | 0.035 | 39.29 | 8904 | 8.25 | 55 |  | 105.77 |  | 6.8 | -3.72 | 0.18 | 101
8/28/2025 08:00 | 6 | 21 | 2.75 | 5.805 | 1.723 | 7.09 | 56 | 1.96 | 70.1 | 0.267 | 0.034 | 39.29 | 8904 | 8.24 | 55 |  | 100.22 |  | 6.81 | -3.72 | 0.18 | 101
8/28/2025 08:15 | 6 | 21 | 2.75 | 5.726 | 1.767 | 7.09 | 56 | 1.96 | 70.1 | 0.267 | 0.034 | 39.29 | 8904 | 8.24 | 55 |  | 100.85 |  | 6.78 | -3.72 | 0.17 | 101
8/28/2025 08:30 | 4 | 21 | 2.75 | 6.241 | 1.849 | 7.08 | 56 | 1.96 | 70.1 | 0.267 | 0.034 | 39.29 | 8904 | 8.23 | 55 |  | 172.94 |  | 6.8 | -3.72 | 0.17 | 101
8/28/2025 08:45 | 3 | 21 | 2.75 | 6.186 | 1.919 | 7.07 | 56 | 1.96 | 70.1 | 0.267 | 0.034 | 39.29 | 8904 | 8.24 | 55 |  | 172.35 |  | 6.79 | -3.72 | 0.17 | 101
8/28/2025 09:00 | 1 | 21 | 2.75 | 6.398 | 1.986 | 7.07 | 56 | 1.96 | 70.1 | 0.267 | 0.034 | 39.29 | 8904 | 8.24 | 55 |  | 176.33 |  | 6.78 | -3.72 | 0.16 | 101
8/28/2025 09:15 | 0 | 21 | 2.75 | 6.417 | 1.99 | 7.07 | 56 | 1.96 | 70.1 | 0.267 | 0.034 | 39.29 | 8904 | 8.24 | 55 |  | 176.92 |  | 6.77 | -3.72 | 0.17 | 101
8/28/2025 09:30 | 6 | 21 | 2.75 | 6.322 | 2.044 | 7.06 | 56 | 1.96 | 70.1 | 0.267 | 0.034 | 39.29 | 8904 | 8.24 | 55 |  | 175.91 |  | 6.76 | -3.72 | 0.17 | 101
8/28/2025 09:45 | 6 | 21 | 2.75 | 5.672 | 2.196 | 7.05 | 56 | 1.96 | 70.1 | 0.267 | 0.034 | 39.29 | 8904 | 8.24 | 55 |  | 158.63 |  | 6.75 | -3.72 | 0.17 | 101
8/28/2025 10:00 | -1 | 21 | 2.75 | 5.977 | 2.267 | 7.06 | 56 | 1.96 | 70.1 | 0.267 | 0.033 | 39.29 | 8904 | 8.24 | 55 |  | 166.22 |  | 6.76 | -3.72 | 0.17 | 101
8/28/2025 10:15 | -2 | 21 | 2.75 | 6.193 | 2.168 | 7.07 | 56 | 1.96 | 70.1 | 0.267 | 0.033 | 39.29 | 8904 | 8.24 | 55 |  | 172.15 |  | 6.76 | -3.72 | 0.2 | 101
8/28/2025 10:30 | 1 | 21 | 2.75 | 6.206 | 2.111 | 7.09 | 56 | 1.96 | 70.1 | 0.267 | 0.033 | 39.29 | 8904 | 8.24 | 55 |  | 172.39 |  | 6.77 | -3.72 | 0.19 | 101
8/28/2025 10:45 | 0 | 21 | 2.75 | 6.188 | 2.022 | 7.09 | 56 | 1.96 | 70.1 | 0.267 | 0.033 | 39.29 | 8904 | 8.24 | 55 |  | 172.7 |  | 6.78 | -3.72 | 0.17 | 101
8/28/2025 11:00 | -1 | 21 | 2.75 | 6.179 | 2.032 | 7.1 | 56 | 1.96 | 70.1 | 0.267 | 0.033 | 39.29 | 8904 | 8.24 | 55 |  | 172.36 |  | 6.77 | -3.72 | 0.19 | 101
8/28/2025 11:15 | 0 | 21 | 2.75 | 6.208 | 2.005 | 7.12 | 56 | 1.96 | 70.1 | 0.267 | 0.032 | 39.29 | 8904 | 8.24 | 55 |  | 172.16 |  | 6.78 | -3.72 | 0.17 | 101